## res
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | TST Test Gas Services Pipework |  | TST Test Gas Services Pipework | 00eb64e7-5feb-4b55-b3e2-a2af255552ce
| section | Details:
| checkpoint | Test Gas Services Pipework checked off as below:
4d166e84-c4e3-58fe-aa0d-b290e2605442 | dropdown | Service Type: | Low Pressure,High Pressure
81317c18-5948-5f6f-a8de-41ee4fee3f5c | dropdown | Test Pressure: | 7kPa,10kPa,20kPa,30kPa,40kPa,50kPa,1.5 x MWP
ab0dfe64-80ad-5a39-b00f-d58ab771e30c | textbox | Location:
d898c82f-1026-5604-90fb-0e3ac5bb183b | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) & ESV Regulations | YES,NO,N/A
4f32bed3-edf4-5f07-8646-548ee153d5bc | button | Installation complies with current drawings & specifications | YES,NO,N/A
1026579c-0d33-53da-9f03-0e41fd903c3d | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
2f07971a-fe6a-5613-ba50-390d83c33983 | button | Testing kit & equipment have current certification | YES,NO,N/A
56eacecc-cb51-50f1-9e6d-8e7ecdfd557b | button | Apply test as per latest revision of AS/NZS 5601.1 (2022) & ESV Regulations (Note: Start & Finish testing photos to be taken only within this Checkpoint) | YES,NO,N/A
| checklist | MET Install Gas Services (Check Meter) |  | MET Install Gas Services (Check Meter) | 0a8c63fa-ce65-48cf-a51a-6152d96c2a24
| section | Details:
| checkpoint | Install Gas Services (Check Meter) checked off as below:
91cc1ef9-fd3f-518f-afd1-52deb2677064 | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
5f8201a8-4a05-5cb6-942a-e271cb52308d | button | Installation complies with current drawings & specifications | YES,NO,N/A
bcd20ccf-8302-55c8-95b2-83d1a83a0998 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
205a49d9-fce3-502c-876d-455623d1108d | button | Check regulatory clearances & distances from building openings, air intakes, etc | YES,NO,N/A
506ed50c-0db1-5b8b-8270-fab2d1a7d011 | button | Check regulatory ventilation if installed indoors | YES,NO,N/A
3b837010-e645-5473-a78d-3454ebf2cfc9 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
d7b2d3ef-8b08-56d8-8152-844f218547a4 | button | Check materials & joining methods | YES,NO,N/A
5a160083-1743-5730-803d-c2ebbdfc5729 | button | Check alignments & levels | YES,NO,N/A
efde12c2-8118-54c6-a3ab-a14898a5d7cc | button | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation | YES,NO,N/A
0ab3e47c-d4cb-5ae7-b93a-9de139b38094 | button | Check meter manifolds for correct height, meter spacing & test points | YES,NO,N/A
e3c8d012-e3fb-5fad-8821-2b12713d2073 | button | Check isolation valves, regulators, connections, etc | YES,NO,N/A
8046a682-5539-5ac6-ae9c-88b1641cdc1e | button | Check colour coding | YES,NO,N/A
c2f6be50-39d0-5f24-b909-6aba40171579 | button | Check pipe labelling | YES,NO,N/A
| checklist | NG Install Gas Services (Rough-ins) |  | NG Install Gas Services (Rough-ins) | 6cb4721d-7c19-4d86-b3c4-368c8246dca6
| section | Details:
| checkpoint | Install Gas Services (Rough-ins) checked off as below:
65bd523c-1eb1-5b8f-89ff-f05ae885284e | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
9fb87e16-87e1-57b9-9b48-d329dc3c94f1 | button | Installation complies with current drawings & specifications | YES,NO,N/A
98362c63-55a8-5892-9561-cec02adf9cf1 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
898be11d-743e-5f92-bd7d-6e8afccf832a | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
4000f90f-aa0d-54b2-892b-6c5ab0b49765 | button | Check pipework can not be holed by plaster screws | YES,NO,N/A
674a76b5-0edb-5efe-afd5-024fde7b97df | button | Check crimp fittings & joints | YES,NO,N/A
2993c273-fc8a-510f-b71f-eb81a747d547 | button | Check for cross connections | YES,NO,N/A
c34006fd-c7ac-5851-9889-7f28d66a860f | button | Check alignment & levels | YES,NO,N/A
abc35e5b-21e0-5c8c-87f3-381b3f399fc0 | button | Check materials & joining methods | YES,NO,N/A
18df5ade-cbd6-5aae-94bb-bae49e2251e1 | button | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation | YES,NO,N/A
ad36162a-7356-536a-83ca-db27f00ca3ff | button | Check isolation valves, pressure regulators, meter assemblies, connections,etc | YES,NO,N/A
2101ab5a-e5d4-5387-96cf-2b88ee114c73 | button | Check lugged elbows & in-wall valves, etc | YES,NO,N/A
deaeec46-8b4a-5003-a260-be7d6fe893fa | button | Check fixture fit-off noggins | YES,NO,N/A
77e87451-1443-5874-8654-06b74ec531fc | button | Check sharp edge pipe protection | YES,NO,N/A
7bcf12b4-09fb-563f-bb40-40ec83298b7b | button | Check pipe colour coding | YES,NO,N/A
3b6c9128-907b-59f9-a570-510ea380486f | button | Check pipe labelling | YES,NO,N/A
e1c1f071-d120-5655-85b4-da93a9cb61d8 | button | Check floor/wall penetration fire proofing | YES,NO,N/A
| checklist | COM Commission Final Handover |  | COM Commission Final Handover | 7031e078-4a4f-4d6e-a705-54cc13830650
| section | Details:
| checkpoint | Commission Final Handover checked off as below:
238e7cc8-86c0-5516-8ad5-6eed1e25c39b | textbox | Location:
e40827a6-215a-5700-9f7d-e951517181ae | button | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022) | YES,NO,N/A
9329d326-ea8c-5e40-a479-749266736658 | button | Installation complies with current drawings & specifications | YES,NO,N/A
f3308e89-e8ff-510f-abff-4b2724d7de74 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
c9c68301-1dcc-59f1-afc3-02efa5a5ce90 | button | Thoroughly check all pipework, fittings, connections, etc for damage or water leaks | YES,NO,N/A
1f235945-d7b5-5875-99f3-fe4d7e2dbdfe | button | Check for any damage or missing components | YES,NO,N/A
709a5c57-c7d6-5092-b847-deab3350dddf | button | Check level & alignment of all fixtures & tapware | YES,NO,N/A
d971c7f3-93f0-5407-a1bc-e9eb8baf3088 | button | Check all fixtures, tapware & components are securely fixed | YES,NO,N/A
8340f5ca-609e-5f9e-b24b-34a5c3583983 | button | Check all mini-stops and valves are fully open | YES,NO,N/A
aafba1a6-5c46-55e0-b77e-48c14dfd9a8b | button | Check all pressure reduction & non-return valves | YES,NO,N/A
954dbc8d-6219-53e5-9029-9a7b5a886e1e | button | Check all flexible connections are not twisted or kinked | YES,NO,N/A
a001f9cc-5d74-50d3-ac1a-2af9e76e9207 | button | Check for water for cross connections | YES,NO,N/A
7db584f7-8d47-5334-870b-eb02fd1e859b | button | Check fixture wastes & connections | YES,NO,N/A
fae09d63-db3a-5932-841c-3b21b3b00653 | button | Check dishwasher drain hose is looped hard-up under bench-top | YES,NO,N/A
cf135084-bdfe-54d7-b9c7-a528447fd336 | button | Check pipework & all traps are clear of debris | YES,NO,N/A
7ec5fcdf-5787-5491-8fbf-f2126ad09b79 | button | Check AAV is installed hard-up under bench-top | YES,NO,N/A
0d251af6-2747-5b8a-9b08-9d19ab6b8c83 | button | Check future connection water valves are securely capped (fridge/washing machine stops) | YES,NO,N/A
2ec14cfd-45cf-52ae-a83c-9b09ab968ad4 | button | Check hot water delivery temperature | YES,NO,N/A
158ca67d-8ee6-591f-83c3-585862919284 | button | Check TV do not exceed 50°C | YES,NO,N/A
f4ba0b2d-7c63-5782-9381-4060cfe9df89 | button | Check TMV do not exceed 45°C | YES,NO,N/A
f3fff008-a786-53cb-830b-d9790cd9e880 | button | Check dishwasher function through short cycle | YES,NO,N/A
36e63210-0558-5387-8661-c1367b9f64c8 | button | Check gas valves & regulators | YES,NO,N/A
9958b8dd-0afa-5e85-9247-6cd9354d32ac | button | Check gas flame stop device | YES,NO,N/A
e6255014-9c39-5b16-977a-2d6e955dba6e | button | Check all gas burner functions | YES,NO,N/A
10570930-f3f6-57c3-a9ff-920c1092adc9 | button | Check balcony hose tap is securely fixed | YES,NO,N/A
706c2cea-4041-5d20-8533-6bb4a6bc9d54 | button | Check balcony floor grate is clear | YES,NO,N/A
0f684756-bd95-5e96-89d0-d12a144d010b | button | Check all downpipes & overflows are fitted correctly | YES,NO,N/A
8acc0a7d-bdb9-5b9d-916c-b4deb40519f8 | button | Check all vents are finished & weather proofed | YES,NO,N/A
69c32c04-6f76-5bc9-9e70-c9e72abec8ac | button | Check all fixtures & tapware function correctly | YES,NO,N/A
a842923c-1690-5bc2-a004-132837103dc4 | button | Check receipt of all Authority sign-off & acceptance documentation | YES,NO,N/A
b9d74e39-0eea-5ffd-a83d-29bceb8e6d02 | button | Check receipt of all manufacturers warranty documentation & owners manuals | YES,NO,N/A
24492dd4-c6a8-5000-a6eb-5bfd06dad0ad | button | Confirm area has been left clean | YES,NO,N/A
| checklist | PE Install Hot Water Generating Plant |  | PE Install Hot Water Generating Plant | 7eb513ef-2d14-44e0-9cdc-de7397cfec4d
| section | Details:
| checkpoint | Install Hot Water Generating Plant checked off as below:
cff2578c-ad2e-5d22-ae43-1183007c7f36 | button | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4, &/or AS/NZS 5601.1 (2022) | YES,NO,N/A
d04ff6b8-3ae2-5b0a-b8fb-39e6338c07ea | button | Installation complies with current drawings & specifications | YES,NO,N/A
be1b7099-e564-5e67-b3b9-6c201a3267ac | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
14045a70-e57e-57dd-85cf-faf06c742905 | button | Check regulatory clearances & distances from building openings & air intakes (Gas HW Plants) | YES,NO,N/A
4e9d27bd-9a96-5cd3-a576-17b860e9f437 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
cd7ee124-f7a0-5862-a1ad-336bcc206338 | button | Check materials & joining methods | YES,NO,N/A
dfb52414-3ce9-5811-b43a-85a7ce1ef116 | button | Check level & alignment | YES,NO,N/A
cf508ffb-0111-56ec-acbd-9b72361e55be | button | Check all pipework, isolation valves, non-return valves, pressure reduction valves, water filters & connections, etc | YES,NO,N/A
597bf0d8-8897-5055-acd2-888a385dff11 | button | Check bold-down & fixing points are secure | YES,NO,N/A
e29d0db1-2ba6-5aca-b295-e6fc646e3a36 | button | Check cable conduits | YES,NO,N/A
0aca9d20-6a38-5eb0-9ac4-be6e298714a9 | button | Check thermal pipe lagging | YES,NO,N/A
26b97e03-2254-5c14-a73d-2c044a57aec0 | button | Check PTR valve, safe tray & drainage | YES,NO,N/A
397db308-d4d0-524b-96a4-ec4cbde268bf | button | Check flexible connections are not twisted or kinked | YES,NO,N/A
f21569b8-bdb8-5462-b997-cc00f5d7a35d | button | Check solar panels & mounting brackets | YES,NO,N/A
61aa97d4-03eb-52be-aef3-ced54fb592c3 | button | Check solar connecting pipework & fittings | YES,NO,N/A
00587bc9-5d42-5323-9375-4cff69ea7bab | button | Check circulation pump installation | YES,NO,N/A
247722bf-1fc1-5b59-becb-a1c1065f219c | button | Check installation of flue system (if applicable) | YES,NO,N/A
809878d0-a1d0-5b01-87b8-bf3869900b93 | button | Check control panel is installed | YES,NO,N/A
bc7cd5fc-11da-5015-bc5a-4d42888ce14d | button | Check power & data cables are run to the control panel | YES,NO,N/A
a2bf80e0-5715-5375-bc85-7b4a2d128aea | button | Check electrical power is available | YES,NO,N/A
3b67c859-1575-5c8f-b56d-187a75cbe14c | button | Check BMS connection is available | YES,NO,N/A
| checklist | COM Commission Hot Water Generating Plant |  | COM Commission Hot Water Generating Plant | a3b5de6d-ffef-40d3-bfd4-ebac372ff64e
| section | Details:
| checkpoint | Commission Hot Water Generating Plant checked off as below:
fcb3875f-d5bc-55b2-ba02-8ba970d435f7 | dropdown | Type: | Commercial Bulk HW Plant (Gas),Commercial Bulk Instantaneous HW Plant (Gas),Commercial Bulk Heat Pump (Elec)
055c6eff-b1e3-5398-ad1e-230bdbe924ba | dropdown | Solar Preheat: | Yes,No
c9edba29-4f14-54c7-8b28-7f7819148f01 | textbox | Location:
dd7a763f-e11e-5832-9493-21cb3c84e139 | button | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022) | YES,NO,N/A
556fc37f-1df4-505a-9565-e01f0273b5bb | button | Installation complies with current drawings & specifications | YES,NO,N/A
f13b1126-46f2-54ee-ac3e-e0047a00d4af | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
46d7c922-d38a-5073-8a40-9797c1c144cc | button | Check regulatory clearances & distances from building openings & air intakes (Gas HW Plants) | YES,NO,N/A
274be54d-e0ff-5b07-b78b-4663a00e5889 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
8543fbf8-b76c-535f-82d4-16afe3e3d666 | button | Check all fixing/hold down points | YES,NO,N/A
f7404af0-a54c-567c-b83f-7aca90ec4404 | button | Check isolation valves are fully open & non-return valves flow direction | YES,NO,N/A
45db94ca-ce3d-590e-8fda-d711d2cd4fc4 | button | Check water filters are clean | YES,NO,N/A
617ffe02-d0a5-5be2-87c2-98a7285ecd9d | button | Check gas valves & connections (if applicable) | YES,NO,N/A
602dbb9b-30cc-502d-9554-5375e60acaf8 | button | Check circulating pumps | YES,NO,N/A
182f4b23-583c-504c-addc-7b9c347db354 | button | Check flue system & operation (if applicable) | YES,NO,N/A
4bda288c-2d40-5666-94e3-fef4e159d2fe | button | Check flow & return temperatures | YES,NO,N/A
8e7a1674-c283-520f-8c42-1bd612ffc8b3 | button | Check solar panels & mounting brackets | YES,NO,N/A
74430c00-6b83-56ee-9338-0cc96b618b96 | button | Check solar connecting pipework & fittings | YES,NO,N/A
3460a619-1084-589c-b0bb-50e084182c5e | button | Check solar circulation pump | YES,NO,N/A
ce48b6eb-1f1e-5cf3-990c-464a449032ba | button | Check auto shut-down system | YES,NO,N/A
0343c077-ecba-5917-981d-8260b1be0e4e | button | Check auto start system | YES,NO,N/A
85dacda4-5665-527a-8c39-06b89dc38d9a | button | Check control panel display | YES,NO,N/A
765c47cb-a558-5553-aa37-88118d1ce673 | button | Check programmed set points | YES,NO,N/A
784b8775-c33e-5d03-ac38-8148397f5f45 | button | Check BMS connection | YES,NO,N/A
f48c624a-e65a-5bae-8515-6df1aa159129 | button | Provide the suppliers commissioning report & all plant documentation to this checkpoint | YES,NO,N/A
| checklist | NG Install Gas Services (Mains/Risers) |  | NG Install Gas Services (Mains/Risers) | b8d1d5c8-8dc8-4e13-8a05-096868766d29
| section | Details:
| checkpoint | Install Gas Services (Mains/Risers) checked off as below:
aacaba46-c515-54c6-b50e-d27b0f98d395 | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
562e97c2-0be8-52de-af16-228bab9cc134 | button | Installation complies with current drawings & specifications | YES,NO,N/A
41c7d5bc-7c9e-5836-9c6e-8f04d0890500 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
4fafca1c-240c-5edf-aeda-f9f0d439a810 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
1bf5e792-b157-59c6-b87b-30a458b7de00 | button | Check materials & joining methods | YES,NO,N/A
e31222c2-d78b-5d96-a34a-8468f8f70ebe | button | Check crimp fittings & joints | YES,NO,N/A
495c1739-954e-5585-8937-045bf296ea52 | button | Check for cross connections | YES,NO,N/A
b8c5b10d-b7ab-5873-a2ab-fe579779f8d0 | button | Check alignments & levels | YES,NO,N/A
dd005c80-6a1e-50c1-a9c6-befb53b9b021 | button | Check expansion joints and anchor points | YES,NO,N/A
5278ef30-ac45-5033-b46e-972371831b6f | button | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation | YES,NO,N/A
5b38cc65-69c8-5805-9afd-106e29cc4f6e | button | Check isolation valves, pressure regulators, meter assemblies, connections,etc | YES,NO,N/A
73869146-caba-5a4c-9b5e-d9ec97cb1a1c | button | Check pipework is clear of debris | YES,NO,N/A
a0218e2e-d73f-575c-8ddc-5ed097fd0d09 | button | Check open ends are sealed | YES,NO,N/A
1c0a41be-d2cf-5c6b-a822-5eccc05848e4 | button | Check pipe colour coding | YES,NO,N/A
7499f4d3-57e7-58aa-9ebb-051fd4f5066b | button | Check pipe labelling | YES,NO,N/A
d1207ff0-a06c-5758-8d10-378d476f1314 | button | Check floor/wall penetration fire proofing | YES,NO,N/A
| checklist | NG Install Gas Services (In-ground) |  | NG Install Gas Services (In-ground) | c75aa42b-5931-4105-845b-2b4cf687adf1
| section | Details:
| checkpoint | Install Gas Services (In-ground) checked off as below:
a245c3c9-d512-5902-86b8-6b51e41e1951 | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
39b071ee-5c73-5704-8949-8e33d31669e8 | button | Installation complies with current drawings & specifications | YES,NO,N/A
a571f096-194c-57ca-a5b1-351a190fd3d7 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
dda56875-a7d6-5dd5-b4bd-8c8be72a5915 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
68aa26a0-ee7f-5133-b18b-f6e7f558d757 | button | Check materials & joining methods | YES,NO,N/A
d5b0012b-048e-5720-b31f-116dee99907e | button | Check alignments & levels | YES,NO,N/A
bcbbbd38-ee00-5e25-b17a-8fac696c9c16 | button | Check trench depth, bedding, service clearances, minimum cover, etc | YES,NO,N/A
8584465a-e4e9-5852-875b-9914b562889f | button | Check isolation valves, connections, etc | YES,NO,N/A
9581d374-78fb-5a6f-97be-185562ff7acf | button | Check pipework is clear of debris | YES,NO,N/A
1564ff5a-10a5-50ab-88d2-ffb8ea582897 | button | Check open ends are sealed | YES,NO,N/A
308e8043-c773-57b3-8665-9f3e64f1d014 | button | Check pipe colour coding | YES,NO,N/A
bdb5bbc4-9bb8-558c-a3dd-241405eabf35 | button | Check pipe trench marking tape | YES,NO,N/A
06c618e3-fa8f-58b1-9145-b8e73184fc7b | button | Check trench backfill & compaction | YES,NO,N/A
| checklist | COM Commission Gas Appliance |  | COM Commission Gas Appliance | cdd62f0c-3eb3-4139-b647-1245f58832f8
| section | Details:
| checkpoint | Commission Gas Appliance checked off as below:
7b8abf23-7c3b-5ec5-ac0a-9428c45208c4 | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
ef36ef4f-89ca-52fe-b54f-498de08ee1ad | button | Installation complies with current drawings & specifications | YES,NO,N/A
d64eb129-893e-5957-ac2a-da5875bf2195 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
b1c3016d-d29c-52f8-a7ae-31ce5066bf5f | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
3d0ad187-798e-54d9-a266-fe33db9d9393 | button | Check fixing points are secure | YES,NO,N/A
a8c9e72f-f9c5-52ec-ac0d-f58aeecfd4db | button | Check level & alignment is correct | YES,NO,N/A
6174d1b4-e914-5428-88b9-e159e939103c | button | Check surrounding wall material is fire rated | YES,NO,N/A
3bcac91d-daf4-519e-8e3a-87ba2ebfa8c7 | button | Check distance from cook-top to range hood complies with manufacturer specification | YES,NO,N/A
dc76eecf-60d8-56a3-9d2f-b74c071899b1 | button | Check surrounding walls to closest burner distance complies with manufacturer specification | YES,NO,N/A
0750a05a-881a-5ac8-a7ea-b94553b6c4b5 | button | Check gas service has been purged | YES,NO,N/A
6be08308-eba8-57fc-8f11-3d2ff541b09d | button | Check flame ignition device | YES,NO,N/A
710b9ae5-7998-5ef2-8ce9-9aecab4e1e4e | button | Check all burners for blockages, etc | YES,NO,N/A
9006490a-8bb1-556d-92a5-29ce5f27061a | button | Check all burners for correct flame operation, height, colour, etc | YES,NO,N/A
07789ccd-ad61-5aad-a8ee-c007abae6fb6 | button | Check flame failure device | YES,NO,N/A
52769bfd-7100-57a9-ad66-a64e965641e3 | button | Check all functions & controls for correct operation | YES,NO,N/A
| checklist | FO Fit-off Gas Appliance |  | FO Fit-off Gas Appliance | e0af0d77-d38b-4a43-982f-6421f10c19cf
| section | Details:
| checkpoint | Fit-off Gas Appliance checked off as below:
d22a01e5-6b35-5c65-86bd-818d27ad9b80 | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
d2632ce9-08f9-58ab-86d9-58483f54329d | button | Installation complies with current drawings & specifications | YES,NO,N/A
07982ed7-3cae-5743-80af-d4145a0bacc8 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
89c608d3-0466-58de-9455-8da70bbf7ff2 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
b36fafac-fcd5-546e-b942-265f559cb52e | button | Check fixing points are secure | YES,NO,N/A
cf31a96c-f95b-5619-8d3e-d18729c7e58f | button | Check level & alignment is correct | YES,NO,N/A
b00824f8-44cc-5204-afdf-88ea3984b015 | button | Check surrounding wall material is fire rated | YES,NO,N/A
1795e819-a595-5451-9606-c9a15e2007a0 | button | Check distance from cook-top to range hood complies with manufacturer specification | YES,NO,N/A
79cd9824-b3cc-5289-9c91-92844c1b0639 | button | Check surrounding walls to closest burner distance complies with manufacturer specification | YES,NO,N/A
267e0fac-81d6-5e54-99b2-e4f88758cb9b | button | Check flexible connections are not twisted or kinked | YES,NO,N/A
0a24bc9e-e275-53bf-990f-189b4aabc477 | button | Check gas isolation valve & cover plate | YES,NO,N/A
02440f04-a8e6-5042-9446-afde71103268 | button | Check gas pressure regulator | YES,NO,N/A
75e5bcc3-a9b0-5e70-8e2e-5df82f69c856 | button | Check flame failure device | YES,NO,N/A
216cd603-5515-5e35-aa10-dd5ebffd94bd | button | Check all functions & controls for correct operation | YES,NO,N/A