## Project Structure
Folder Structure | [6 empty] | Checklists
30551 - Coles Spoke Fitout
ITP Setout
Site QA
| Rough-In | Main Heading Name | Sub Heading Name | Equipment Name | Drawing Number | ITP Name
VRF Air Conditioning Units
VRF Fan Coil Units
|  |  |  | FCU 1.1.1 GF - Driver | M150 | Ducted Unit ITP RI
|  |  |  | FCU 1.1.2 GF - Entry | M150 | Ducted Unit ITP RI
|  |  |  | FCU 1.1.3 GF - CD Office | M150 | Ducted Unit ITP RI
|  |  |  | FCU 1.1.4 FF - Lunch | M150 | Ducted Unit ITP RI
|  |  |  | FCU 1.1.5 FF - Corridor | M150 | Ducted Unit ITP RI
|  |  |  | FCU 1.1.6 FF - Agility | M150 | Ducted Unit ITP RI
|  |  |  | FCU 1.1.7 FF - Meeting | M150 | Ducted Unit ITP RI
|  |  |  | FCU 1.1.8 FF Training | M150 | Ducted Unit ITP RI
VRF Branch Units
|  |  |  | BSU-1.1 GF | M150 | BSU ITP RI
|  |  |  | BSU-1.2 FF | M150 | BSU ITP RI
VRF Condenser
|  |  |  | CU-1 | M150 | Condenser ITP RI
Split System Air Conditioning Units
|  |  |  | ACU-1.2 GF Comms RM | M150 | HWall Split ITP RI
|  |  |  | ACU-1.3 GF Comms RM | M150 | HWall Split ITP RI
|  |  |  | ACU-1.4 GF Dock Office | M110 | Cass/Split ITP RI
|  |  |  | ACU-1.5 GF Dock Lunch RM | M110 | Cass/Split ITP RI
Ventilation Fans
|  |  |  | OAF-G.4 GF Coles Dock Office | M110 | Vent Fan ITP RI
|  |  |  | OAF-G.5 GF Coles Cleaners RM | M110 | Vent Fan ITP RI
|  |  |  | TEF-G.2 Coles WHSE Amenities | M110 | Vent Fan ITP RI
|  |  |  | TEF-G.3 Coles Office Amenities | M150 | Vent Fan ITP RI
|  |  |  | EF-G.4 Coles Cleaners RM | M110 | Vent Fan ITP RI
|  | Electrical Boards |  | T-1.1 Warehouse Adjacent Main Office | M150 | Electrical Board ITP RI
|  |  |  | T-1.2 Dock Office | M110 | Electrical Board ITP RI
| Fit-Off | Main Heading Name | Sub Heading Name | Equipment Name | Drawing Number | ITP Name
VRF Air Conditioning Units
VRF Fan Coil Units
|  |  |  | FCU 1.1.1 GF - Driver | M150 | Ducted Unit ITP FO
|  |  |  | FCU 1.1.2 GF - Entry | M150 | Ducted Unit ITP FO
|  |  |  | FCU 1.1.3 GF - CD Office | M150 | Ducted Unit ITP FO
|  |  |  | FCU 1.1.4 FF - Lunch | M150 | Ducted Unit ITP FO
|  |  |  | FCU 1.1.5 FF - Corridor | M150 | Ducted Unit ITP FO
|  |  |  | FCU 1.1.6 FF - Agility | M150 | Ducted Unit ITP FO
|  |  |  | FCU 1.1.7 FF - Meeting | M150 | Ducted Unit ITP FO
|  |  |  | FCU 1.1.8 FF Training | M150 | Ducted Unit ITP FO
VRF Branch Units
|  |  |  | BSU-1.1 GF | M150 | BSU ITP FO
|  |  |  | BSU-1.2 FF | M150 | BSU ITP FO
VRF Condenser
|  |  |  | CU-1 | M150 | Condenser ITP FO
Split System Air Conditioning Units
|  |  |  | ACU-1.2 GF Comms RM | M150 | HWall Split ITP FO
|  |  |  | ACU-1.3 GF Comms RM | M150 | HWall Split ITP FO
|  |  |  | ACU-1.4 GF Dock Office | M110 | Cass/Split ITP FO
|  |  |  | ACU-1.5 GF Dock Lunch RM | M110 | Cass/Split ITP FO
Ventilation Fans
|  |  |  | OAF-G.4 GF Coles Dock Office | M110 | Vent Fan ITP FO
|  |  |  | OAF-G.5 GF Coles Cleaners RM | M110 | Vent Fan ITP FO
|  |  |  | TEF-G.2 Coles WHSE Amenities | M110 | Vent Fan ITP FO
|  |  |  | TEF-G.3 Coles Office Amenities | M150 | Vent Fan ITP FO
|  |  |  | EF-G.4 Coles Cleaners RM | M110 | Vent Fan ITP FO
|  | Electrical Boards |  | T-1.1 Warehouse Adjacent Main Office | M150 | Electrical Board ITP FO
|  |  |  | T-1.2 Dock Office | M110 | Electrical Board ITP FO
| Commissioning | Main Heading Name | Sub Heading Name | Equipment Name | Drawing Number | ITP Name
VRF Air Conditioning Units
VRF Fan Coil Units
|  |  |  | FCU 1.1.1 GF - Driver | M150 | Ducted Unit ITP Comm
|  |  |  | FCU 1.1.2 GF - Entry | M150 | Ducted Unit ITP Comm
|  |  |  | FCU 1.1.3 GF - CD Office | M150 | Ducted Unit ITP Comm
|  |  |  | FCU 1.1.4 FF - Lunch | M150 | Ducted Unit ITP Comm
|  |  |  | FCU 1.1.5 FF - Corridor | M150 | Ducted Unit ITP Comm
|  |  |  | FCU 1.1.6 FF - Agility | M150 | Ducted Unit ITP Comm
|  |  |  | FCU 1.1.7 FF - Meeting | M150 | Ducted Unit ITP Comm
|  |  |  | FCU 1.1.8 FF Training | M150 | Ducted Unit ITP Comm
VRF Branch Units
|  |  |  | BSU-1.1 GF | M150 | BSU ITP Comm
|  |  |  | BSU-1.2 FF | M150 | BSU ITP Comm
VRF Condenser
|  |  |  | CU-1 | M150 | Condenser ITP Comm
Split System Air Conditioning Units
|  |  |  | ACU-1.2 GF Comms RM | M150 | HWall Split ITP Comm
|  |  |  | ACU-1.3 GF Comms RM | M150 | HWall Split ITP Comm
|  |  |  | ACU-1.4 GF Dock Office | M110 | Cass/Split ITP Comm
|  |  |  | ACU-1.5 GF Dock Lunch RM | M110 | Cass/Split ITP Comm
Ventilation Fans
|  |  |  | OAF-G.4 GF Coles Dock Office | M110 | Vent Fan ITP Comm
|  |  |  | OAF-G.5 GF Coles Cleaners RM | M110 | Vent Fan ITP Comm
|  |  |  | TEF-G.2 Coles WHSE Amenities | M110 | Vent Fan ITP Comm
|  |  |  | TEF-G.3 Coles Office Amenities | M150 | Vent Fan ITP Comm
|  |  |  | EF-G.4 Coles Cleaners RM | M110 | Vent Fan ITP Comm
|  | Electrical Boards |  | T-1.1 Warehouse Adjacent Main Office | M150 | Electrical Board ITP Comm
|  |  |  | T-1.2 Dock Office | M110 | Electrical Board ITP Comm

## Checklists
Rough-In ITPs
type | name | values
checklist | Ducted Unit ITP RI
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | GreenStar - Duct Delivery
section | Rough-In
checkpoint | Unit has clearance from other services
checkpoint | Correct Fan Coil Installed - take photo of data plate
checkpoint | FCU installed with anti vibration mounts
checkpoint | SA and RA Boxes fitted with anti vibration mounts
checkpoint | RA Box has filters
checkpoint | FCU Installed in accordance with Seismic Design Drawing
checkpoint | Refrigeration Pipe work installed securely with insulation
checkpoint | Tundish Available
checkpoint | Drain Pipe work installed and insulated to tundish
checkpoint | Electrical supply cabling installed with isolation point (isolation point labelled)
checkpoint | Interconnect and Control Cabling installed and secured
checkpoint | Check Access to Filters and Electrical Box
checkpoint | Ductwork installed with clearance from other services
checkpoint | Ductwork Joints Sealed
checkpoint | Ductwork adequately supported
checkpoint | All spigots protected from dust ingress
checkpoint | Flex Installed and Supported with Gutter Guard or equivalent
checkpoint | Provisions for future access are adequate
checkpoint | Ready for Ceiling and Wall Sheeting
checklist | BSU ITP RI
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Rough-In
checkpoint | Unit has clearance from other services
checkpoint | Correct Branch Unit Installed - take photo of data plate
checkpoint | BSU installed with anti vibration mounts
checkpoint | BSU Installed in accordance with Seismic Design Drawing
checkpoint | Refrigeration Pipe work installed securely with insulation
checkpoint | Tundish Available
checkpoint | Drain Pipe work installed and insulated to tundish
checkpoint | Electrical supply cabling installed with isolation point (isolation point labelled)
checkpoint | Interconnect and Control Cabling installed and secured
checkpoint | Ready for Ceiling and Wall Sheeting
checklist | Condenser ITP RI
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Rough-In
checkpoint | Unit has clearance from other services
checkpoint | Correct Condenser Installed - take photo of data plate
checkpoint | Condenser Feet installed with anti vibration mounts
checkpoint | Condenser Installed in accordance with Seismic Design Drawing
checkpoint | Tundish Available
checkpoint | Electrical supply cabling installed with isolation point (isolation point labelled)
checkpoint | Interconnect and Control Cabling installed and secured
checklist | Highwall Split ITP RI
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Rough-In
checkpoint | Unit has clearance from other services
checkpoint | Correct Fan Coil Installed - take photo of data plate
checkpoint | Correct Condenser Installed - take photo of data plate
checkpoint | Condenser installed with correct mounting feet.
checkpoint | Condenser Installed in accordance with Seismic Design Drawing
checkpoint | Refrigeration Pipe work installed securely with insulation
checkpoint | Tundish Available
checkpoint | Drain Pipe work installed and insulated to tundish
checkpoint | Electrical supply cabling installed with isolation point (isolation point labelled)
checkpoint | Interconnect and Control Cabling installed and secured
checkpoint | Ready for Ceiling and Wall Sheeting
checklist | Cass/Split ITP RI
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Rough-In
checkpoint | Unit has clearance from other services
checkpoint | Correct Fan Coil Installed - take photo of data plate
checkpoint | Fan Coil installed with anti vibration mounts
checkpoint | Correct Condenser Installed - take photo of data plate
checkpoint | Condenser installed with correct mounting feet.
checkpoint | Condenser Installed in accordance with Seismic Design Drawing
checkpoint | Refrigeration Pipe work installed securely with insulation
checkpoint | Tundish Available
checkpoint | Drain Pipe work installed and insulated to tundish
checkpoint | Electrical supply cabling installed with isolation point (isolation point labelled)
checkpoint | Interconnect and Control Cabling installed and secured
checkpoint | Ready for Ceiling and Wall Sheeting
checklist | Vent Fan ITP RI
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | GreenStar - Duct Delivery
section | Rough-In
checkpoint | Unit has clearance from other services
checkpoint | Correct Fan Installed - take photo of data plate
checkpoint | Fan installed with anti vibration mounts
checkpoint | Fan and Duct Installed in accordance with Seismic Design Drawing
checkpoint | Electrical supply cabling installed with isolation point (isolation point labelled)
checkpoint | Control Cabling installed and secured
checkpoint | Check Access to Fan - Mark Access Panel if required
checkpoint | Ductwork installed with clearance from other services
checkpoint | Ductwork Joints Sealed
checkpoint | Ductwork adequately supported
checkpoint | All spigots open 100% and protected from dust ingress
checkpoint | Flex Installed and Supported with Gutter Guard or equivalent
checkpoint | Provisions for future access are adequate
checkpoint | Ready for Ceiling and Wall Sheeting
checklist | Electrical Board ITP RI
section | General
checkpoint | Area ready and accessible for work - take picture if required
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
section | Rough-In
checkpoint | Electrical Board has the correct Clearance from other Services
checkpoint | Electrical Board Installed in accordance with Seismic Design Drawing
checkpoint | Cable Tray Installed where Required
checkpoint | Provisions for future access are adequate
checkpoint | Ready for Ceiling and Wall Sheeting
Fitoff ITPs
type | name | values
checklist | Ducted Unit ITP FO
section | Fit-Off
checkpoint | Grilles and Cushion Boxes Installed
checkpoint | Adequate Access Achieved
checkpoint | Condensate drains from drain tray
checkpoint | Drain Terminated to Tundish
checkpoint | Wall Controller Installed and labelled
checklist | BSU ITP FO
section | Fit-Off
checkpoint | Adequate Access Achieved
checkpoint | Drain Terminated to Tundish
checklist | Condenser ITP FO
section | Fit-Off
checkpoint | Electrical and Control Terminations Complete
checkpoint | Refrigeration Pipe work installed securely with insulation
checkpoint | Correct Master Condenser Installed - take picture of data plate
checkpoint | Correct Slave Condenser Installed - take picture of data plate
checkpoint | Drain Terminated to Tundish
checklist | Highwall Split ITP FO
section | Fit-Off
checkpoint | Fan Coil Installed
checkpoint | FCU Drain Terminated to Tundish
checkpoint | Condensate drains from drain tray
checkpoint | Wall Controller Installed and labelled
checklist | Cass/Split ITP FO
section | Fit-Off
checkpoint | Fan Coil Installed
checkpoint | FCU Drain Terminated to Tundish
checkpoint | Condensate drains from drain tray
checkpoint | Wall Controller Installed and labelled
checklist | Vent Fan ITP FO
section | Fit-Off
checkpoint | Grilles and Cushion Boxes Installed
checkpoint | Adequate Access Achieved
checkpoint | Wall Controller Switch is Installed if Required
checklist | Electrical Board ITP FO
section | Fit-Off
checkpoint | Cable Containment has been completed
checkpoint | Mains Supply provided by House Electrical Contractor
checkpoint | All Terminations Complete
Commissioning ITPs
type | name | values
checklist | Ducted Unit ITP Comm
section | Commissioning
checkpoint | Electrical Commissioning Complete
checkpoint | Refrigeration Commissioning Complete
checkpoint | Clear Access is Achieved
checkpoint | Unit Test Run on Heating for 2 hours
checkpoint | Unit Test Run on Cooling for 2 hours
checkpoint | Air Balance Complete
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | BSU ITP Comm
section | Commissioning
checkpoint | Electrical Commissioning Complete
checkpoint | Refrigeration Commissioning Complete
checkpoint | Clear Access is Achieved
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Condenser ITP Comm
section | Commissioning
checkpoint | Electrical Commissioning Complete
checkpoint | Refrigeration Commissioning Complete
checkpoint | Units Test Run on Heating for 2 hours
checkpoint | Units Test Run on Cooling for 2 hours
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Highwall Split ITP Comm
section | Commissioning
checkpoint | Electrical Commissioning Complete
checkpoint | Refrigeration Commissioning Complete
checkpoint | Condenser drain terminated to tundish
checkpoint | Unit Test Run on Heating for 2 hours
checkpoint | Unit Test Run on Cooling for 2 hours
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Cass/Split ITP Comm
section | Commissioning
checkpoint | Electrical Commissioning Complete
checkpoint | Refrigeration Commissioning Complete
checkpoint | Condenser drain terminated to tundish
checkpoint | Unit Test Run on Heating for 2 hours
checkpoint | Unit Test Run on Cooling for 2 hours
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Vent Fan ITP Comm
section | Commissioning
checkpoint | Electrical Commissioning Complete
checkpoint | Unit Test Run - Works as Designed
checkpoint | Clear Access is Achieved
checkpoint | Air Balance Complete
checkpoint | Handover - Work completed as per specification, checked and accepted
checklist | Electrical Board ITP Comm
section | Commissioning
checkpoint | Electrical Commissioning Complete by Licensed Electrical Contractor
checkpoint | All systems tested and working as designed
checkpoint | Handover - Work completed as per specification, checked and accepted