## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
3ac3bb63-645a-53dc-b336-a0320ee14cd2 | checklist-flat | Fire Service BG |  | Fire Service BG
083eb9c4-fa14-554f-aec0-197652d9497a | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
| checkpoint | Notify and gain permit from principal contractor / client for inspection (hold point)
| signoff | Notify and gain permit from principal contractor / client for inspection
c14305f2-9ed6-5c66-ba84-f6e1dbe68b58 | checkpoint | Setout & alignment as per drawing (include revision below)
773e22ae-338e-5c21-acf6-79181698c09e | textbox | Drawing & revision number(s)
4fc0f552-afec-541b-b654-572f8de432eb | checkpoint | Correct material as per sample register
2ed31540-094b-5126-866c-4e3adfae1a16 | checkpoint | Bedding material installed correctly
2a76a8df-eec9-5f77-a2d0-6c08c6872dc5 | checkpoint | Fittings & joints correctly installed to manufacturer's requirements
797f3654-d0d8-5d28-97d8-43f3007f39cb | checkpoint | Satisfactory welding/pressing of copper pipe
6bdd26cb-9431-532b-86a8-eb6217f929f5 | checkpoint | Witness marks visible
87476593-2814-5f55-970f-251784096def | checkpoint | Pipework layed correctly & to AS 3500
2f08ca4b-41a3-5245-8ea6-b8ce1e29d68e | checkpoint | Concrete anchor thrust blocks installed as per engineers report
7d844f12-7fa0-53c4-afcf-b4e36e38b33f | checkpoint | Testing to 1700 kPa with no leaks for 120 minutes
5419071a-4563-56ca-be84-852b1e1ec9f0 | checkpoint | Identification of services via I.D tape
d08a8101-0125-591f-9180-7d0df9eb5033 | checkpoint | Backfill & compaction to specification in 300mm layers
a51941bf-58da-55a5-9a43-3db39640fbb2 | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
3d867dea-2eb3-53a0-b65c-5385813173a7 | note | Passing above includes Builder sign-off
7844d696-5542-5006-b1e1-3ca8caf379a1 | tickbox | Area clean