## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
61261eb2-6af1-5bab-9ee2-2b48c37f7838 | checklist | Fix 1 Checklist |  | Fix 1 Checklist
f8bfbdc9-8053-58bd-a022-baeeb34ce428 | section | Sewer AG
083eb9c4-fa14-554f-aec0-197652d9497a | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
| checkpoint | Notify and gain permit from principal contractor / client for inspection (hold point)
| signoff | Notify and gain permit from principal contractor / client for inspection
c14305f2-9ed6-5c66-ba84-f6e1dbe68b58 | checkpoint | Setout & alignment as per drawing (include revision below)
72276118-d3d9-5547-be32-01e122894e62 | textbox | Drawing & revision number(s)
ce322e6d-7f63-5bf6-a477-b5f1a151ddbc | checkpoint | Grades, fittings & joints installed to standards
410bf4a7-cdb4-5244-8684-ed3de2b0fb1a | checkpoint | Fixings & seismic support to standards
65c25f8f-22a4-5daa-a14b-2023299a2c1d | checkpoint | Expansion joints per floor installed correctly & clipped
af8e630c-839c-5cad-bff7-e6f0b9c48092 | checkpoint | Pipe risers sealed per floor & capped off to prevent damage
e0f8ec9c-302d-5bb0-8eb3-f4e80b61eade | checkpoint | Correct invert level (As per Standards)
6a147b79-3c3a-5107-9ae1-c708993977f5 | checkpoint | Vents and AAV installed (As per Standards)
58c39949-84e1-5bec-9481-afb3069adeb5 | checkpoint | Acoustic lagging installed to acoustic specification
0eb38021-b577-5e0e-8e61-1868053ab9b4 | checkpoint | Pipework water tested to 15Kpa
7a255cfd-1417-58ed-a027-9a1a06843d91 | checkpoint | Identifications of services
a51941bf-58da-55a5-9a43-3db39640fbb2 | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
e101fc39-e2df-57dc-ba78-13b0627bc7d3 | note | Passing above includes Builder sign-off
b7d7749f-dff4-5731-9568-de08012a748e | tickbox | Area clean
2d247e4b-4643-55a7-be5d-495d22790e4d | section | Stormwater AG
ed0d47fe-ff4b-4d3a-a1cc-17944c433991 | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
| checkpoint | Notify and gain permit from principal contractor / client for inspection (hold point)
| signoff | Notify and gain permit from principal contractor / client for inspection
51d54e2b-ee8e-4180-8166-b5dee12f200a | checkpoint | Setout & alignment as per drawing (include revision below)
731c34a3-433b-5d6e-9e0e-eacdba234e7d | textbox | Drawing & revision number(s)
1427a3fd-c38d-5ebf-928c-558a4f7ed9e4 | checkpoint | Grades (as per AS:3500)
0425c0ef-7719-51c7-a7b1-b1b2088c7aef | checkpoint | Location (as per hydraulic drawing)
182d568a-531b-5324-9c27-38eb42b6ef9c | textbox | Location
ff9a4ff9-5c7f-5393-9b60-ac364ef2382f | checkpoint | Fixings - Securely fixed (As per Standards)
e4b22e0b-ecbc-5c4f-88db-9e20d3816be8 | checkpoint | Fittings Joints ETC (as per AS 3500)
74b93783-f04a-59f9-9fd8-f08523d1dab8 | checkpoint | Inspection prior to closure
1ef7c64e-399c-5102-b940-881f03e5c003 | checkpoint | Operation of pumps (Commissioning report) if Applicable
9cf7d1b0-458e-528d-9e9d-c7fa76bd2c7a | checkpoint | Test water and discharge requirements are met
a135d123-824b-556f-bb88-5a1febc2ba07 | checkpoint | Correct invert level AS per AS 3500
5329808e-7449-450e-a7a3-c2db7d98783e | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
9744e09c-39de-5a84-965f-c82542d952f0 | note | Passing above includes Builder sign-off
d22d4cc5-aca1-5312-9ca8-70e30408a433 | tickbox | Area clean
659cf882-47fb-5779-a0de-5900f1f92fd3 | section | Rough In
0867b2e7-36dd-4bf0-a428-8808dde43291 | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
| checkpoint | Notify and gain permit from principal contractor / client for inspection (hold point)
| signoff | Notify and gain permit from principal contractor / client for inspection
88ef6fd4-6501-4c66-af24-41d9f7752e50 | checkpoint | Setout & alignment as per drawing (include revision below)
158b76e3-be91-5355-a271-0090670d56aa | textbox | Drawing & revision number(s)
d9ac4413-d238-59a4-b98d-983141533a2c | checkpoint | Material type (as per sample submission)
080af063-649e-586e-8d35-309a1a84fbda | checkpoint | Pipework installation checked against standards (as per AS 3500.1)
801a3b0d-b193-55e7-a017-ac6d43d66cc7 | checkpoint | Welding / pressfit / push fit / witness marks (as per AS 3500.1)
70065ae0-8017-5658-b365-984b8c1474cb | checkpoint | Support & fixings checked (acoustic / seismic / water hammer/ silicone)
2a38040a-3343-5d0a-90af-6a08e88a21a2 | checkpoint | Check for no cross connection
72f3c870-8985-5ea8-acf6-7ed803653557 | checkpoint | Heights double checked before room sign off as per sample submission
ed177efa-6244-50b7-9c64-68476a075087 | checkpoint | Pipe risers water sealed per floor and capped off to prevent damage
f7e73412-8aa9-5e2d-a27f-e5b3eca8bfc2 | checkpoint | Correct sewer ventilation
6e02cdeb-70f0-5c38-8fc1-13b3b41b9393 | checkpoint | Pressure test water lines to (1500kpa)
6fff9bea-2a31-551d-96df-36b4e7276458 | checkpoint | Identification of services
ec5c5a6f-1a76-48cd-bcdb-e242a2c4dc8e | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
63f584c4-8979-5870-ab9b-e43d94b38c87 | note | Passing above includes Builder sign-off
316ad6c9-7a3f-5e27-a836-f32b1c15abfa | tickbox | Area clean
2a3cedb6-ace6-5ceb-93e1-9888017183e2 | section | Rainwater
7295400c-d326-496e-902d-acf376eddbe3 | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
| checkpoint | Notify and gain permit from principal contractor / client for inspection (hold point)
| signoff | Notify and gain permit from principal contractor / client for inspection
e857c810-f7c5-4060-92ea-d74ab08c25ab | checkpoint | Setout & alignment as per drawing (include revision below)
39bcf99b-c78d-52af-8afa-4bb7486f2bcc | textbox | Drawing & revision number(s)
09117d16-dfa2-50b1-bd6e-48ad77253238 | checkpoint | Material type as per approved sample submission
b3af4620-6bbf-5799-a411-13600fc22da4 | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6)
1d31dec7-a3e3-542e-972a-be20964718a6 | checkpoint | Welding / pressfit / push fit (as per AS 3500.1)
0cfbef0b-fc60-5c64-928d-cf19e6487023 | checkpoint | Support & fixings (acoustic / seismic / water hammer)
4731048f-36da-51bd-ad5f-526936078ce5 | checkpoint | Pipework Installation (as per AS 3500.1)
5f445bf0-7c65-5ebf-86df-b16d210f8575 | checkpoint | Check no cross connection
d20132f4-2356-54f0-be61-143c1852c66f | checkpoint | Pressure test (1500kpa pressure test)
6976edca-1a65-4a19-97b6-831b5af36376 | checkpoint | Identifications of services
f4e62eef-edb9-48f6-ab45-3af5533bb724 | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
77f9838d-58b2-57b6-bc60-9aad782ae6e4 | note | Passing above includes Builder sign-off
645c65ef-478d-566b-b14d-6582608fcd2f | tickbox | Area clean