## Table 1
[9 empty] | Inspection and Test Plan - Control and Supervision of the Works | [25 empty] | Doc ID: FH-ZU2-QU-ITP041 REV: 0
Client: Melbourne Airport | [15 empty] | Contract No: CP14038-01 | [13 empty] | Prepared By: Giuliano Follacchio
Project: Taxiway Zulu | [24 empty] | Reviewed By: Jason Lee | [9 empty] | Date: 26/7/24
Construction Process: AGL Pit Fit Out | [24 empty] | Approved By: Giuliano Follacchio | [9 empty] | Date: 26/7/24
Specifications: ZULU-BECA-001-SPC-00004
Structure / Component: AGL
Lot No: Lot Details: Lot size/Quantity: Date:
Item No. |  | Task/Activity Description |  |  |  | Inspection/Test | [22 empty] | HP/ WP/ AP/ IP/ TP/ SCP |  |  | Responsibility Project Engineer Principal’s Representative Surveyor Foreman |  | Checked by:
[6 empty] | Frequency |  |  | Acceptance Criteria | [7 empty] | Reference Documents |  |  |  |  | Inspection/ Test Method |  |  | Record of conformity | [8 empty] | Avionics |  | Principal’s Rep. | FH | Date
1 |  | Preliminary Works
1.1 |  | Check for Correct Documentation |  |  |  | Prior to start |  |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. | [7 empty] | Drawings / Aconex Register |  |  |  |  | Verify |  |  | Drawings and drawing registers |  |  |  | HP* |  |  | Project Engineer
1.2 |  | Implementation of all measures and controls |  |  |  | Prior to start |  |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP | [7 empty] | PSP, EMP, TMP, JSEA, SWMS, WP |  |  |  |  | Visual Inspection |  |  | This ITP signed |  |  |  | HP* |  |  | Project Engineer
1.3 |  | Definition of the work area & survey check |  |  |  | Prior to start |  |  | Work area has been cleared and surveyed (marked on site). Work area to be clearly defined as per For Construction drawings prior to trenching and install. Ensure excavation permit obtained and (if required) services in work(s) area isolated. | [7 empty] | IFC Drawings Excavation Permit |  |  |  |  | Verify |  |  | This ITP signed |  |  |  | SCP |  |  | Project Engineer / Surveyor
2 |  | Installation of SIT Pits
2.1 |  | Pit excavation and placement |  |  |  | Each Lot |  |  | Dig zone marked out and excavation undergone in accordance to relevant permit. Pit placed and levelled as per survey set out. | [7 empty] | Drawings |  |  |  |  | Verify |  |  | This ITP signed Avionics SIT Pit Installation checklist |  |  |  | HP* |  |  | Project Engineer / Surveyor
2.2 |  | Conduit positioning |  |  |  | Each Lot |  |  | Primary and secondary conduits positioned in pit according to IFC drawings. | [7 empty] | Drawings |  |  |  |  | Verify |  |  | This ITP signed Avionics SIT Pit Installation checklist |  |  |  | IP |  |  | Project Engineer
2.3 |  | Bedding and backfill of pit surrounds |  |  |  | Each Lot |  |  | Each pit shall be bedded and backfilled with stabilised sand. | [7 empty] | ZULU- BECA-001- SPC-00004 |  |  |  |  | Verify |  |  | This ITP signed Avionics SIT Pit Installation checklist |  |  |  | HP* |  |  | Project Engineer / Site Supervisor
2.4 |  | Pit number labelling |  |  |  | Each Lot |  |  | Each pit shall be painted with the pit number with black waterproof paint on the inside and top half of the pit wall. Characters shall be 50mm high. | [7 empty] | Drawings |  |  |  |  | Verify |  |  | This ITP signed Avionics SIT Pit Installation checklist |  |  |  | IP |  |  | Project Engineer / Site Supervisor
2.5 |  | Pit close out |  |  |  | Each Lot |  |  | Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished. | [7 empty] | ZULU- BECA-001- SPC-00004 |  |  |  |  | Verify |  |  | This ITP signed Avionics SIT Pit Installation checklist |  |  |  | IP |  |  | Project Engineer
3 |  | Earthing & Fit Out
3.1 |  | Earthing & pit fit out |  |  |  | Each Lot |  |  | If no SITs: - 16mm Earth Cable Terminated From Earth Rod to Earth Bar If pit houses SIT: - 6mm Earth Cable Installed From Earth Bar to SIT, 10 holes to be pre drilled into Earth Bar - SIT Mounting Tray Installed - SIT installed on the same tray which supply different circuits to have a 300mm gap clearance (Second tray to be provided if 300mm separation cannot be achieved on a single layer) | [7 empty] | Drawings ZULU- BECA-001- SPC-00004 |  |  |  |  | Verify |  |  | This ITP signed ADBSG Earthing & Pit Fit Out checklist |  |  |  | IP |  |  | Project Engineer
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
Content ID:AU_00002009 Revision: 5 | [9 empty] | This is an uncontrolled copy if photocopied or printed from the Intranet. Copyright © 2009, Fulton Hogan Ltd. All rights reserved. | [16 empty] | Revised 12-06-2012 Page 3 of 4
[9 empty] | Inspection and Test Plan - Control and Supervision of the Works | [25 empty] | Doc ID: FH-ZU2-QU-ITP041 REV: 0
Client: Melbourne Airport | [15 empty] | Contract No: CP14038-01 | [13 empty] | Prepared By: Giuliano Follacchio
Project: Taxiway Zulu | [24 empty] | Reviewed By: Jason Lee | [9 empty] | Date: 26/7/24
Construction Process: AGL Pit Fit Out | [24 empty] | Approved By: Giuliano Follacchio | [9 empty] | Date: 26/7/24
Specifications: ZULU-BECA-001-SPC-00004
Structure / Component: AGL
HP |  | Hold Point |  |  | Work shall not proceed past the HP until released by the Principal’s Representative | [14 empty] | IP |  |  | Inspection point |  |  |  |  | Formal Inspection to be done and recorded
HP* |  | Fulton Hogan Hold Point |  |  | Work shall not proceed past the HP* until released by Fulton Hogan | [14 empty] | TP |  |  | Test Point |  |  |  |  | Product compliance test to be undertaken and recorded/reported
WP |  | Witness Point |  |  | An inspection which must be witnessed by the Principal’s Representative | [14 empty] | SCP |  |  | Survey conformance point |  |  |  |  | A qualified surveyor to check product/section/structure and report
AP |  | Approval Point |  |  | Written or verbal approval given by the Principal’s Representative
Notes
This is an uncontrolled copy if photocopied or printed from the Intranet. Copyright © 2009, Fulton Hogan Ltd. All rights reserved.
Content ID:AU_00002009 Revision: 5 | [29 empty] | Revised 12-06-2012 Page 4 of 4
SIT Pit Installation
Pit ID:
Pit Type:
Class:
Manufacturer:
Task Details | [14 empty] | Signature: |  |  | Date: | [5 empty] | Name: | [6 empty] | Status:
Task number 1: PRE-WORKS - Survey Pit Position (by Fulton Hogan). - Excavation Permit completed and approved for works (by Fulton Hogan). - Isolation of all services in works area (if required).
Task number 2: CIVIL WORKS - Excavate hole for pit. As per drawings (approx. 1250mm x 1250mm x 1100mm excavation). - Position stabilised sand in excavation and level as per spec. - Lift Pit into position, using the correct lifting method. Ensuring the conduit holes align as per location requirements. - Ensure Pit is level and flush with surrounding ground level.
Task number 3: CIVIL WORKS - Excavate and install earth pit as per the drawings. - Position conduits ensuring they correct align for primary, secondary and earth pit connection. - Install earth bar in SIT Pit. - Position brackets for SIT Mountings.
Task number 4: CIVIL WORKS - Backfill around pit with stabilised sand. - Position pit lids. - Clean area and demobilize.
Task number 5: CIVIL WORKS - Install PIT Labels.
Task number 6: CIVIL WORKS - Install Directional Arrows.
Task number 7: CIVIL WORKS - Install earth stake in earth pit.
Page: 1 | [13 empty] | Asset:
|  |  |  | INSPECTION AND TEST PLAN - 113 Earthing & Pit Fit Out | [21 empty] | Page | [5 empty] | 1 of 2
[26 empty] | Issue Date | [5 empty] | 2024-03-30
[26 empty] | Revision | [5 empty] | 1
REPORT DETAILS |  |  |  | Date Completed | [16 empty] | Drawing References |  |  |  |  | ZULU-BECA-024-DWG
|  |  |  | Project | [6 empty] | Taxiway Zulu 2.0 | [9 empty] | Sheet Completed by
Location on Site
WORK DETAILS | [20 empty] | Legend |  |  |  |  | ✓ yes ✗ no NA not applicable
If no SITs are housed | [10 empty] | If Pit houses SIT | [20 empty] | NOTES
Pit Number |  |  |  | 16mm Earth Cable Terminated From Earth Rod to Earth Bar | [6 empty] | 6mm Earth Cable Installed From Earth Bar to SIT | [9 empty] | SIT Mounting Tray Installed
|  |  |  | INSPECTION AND TEST PLAN Earthing & Pit Fit Out | [21 empty] | Page | [5 empty] | 2 of 2
[26 empty] | Issue Date | [5 empty] | 2024-03-30
[26 empty] | Revision | [5 empty] | 1
WORK DETAILS | [20 empty] | Legend |  |  |  |  | ✓ yes ✗ no NA not applicable
If no SITs are housed | [10 empty] | If Pit houses SIT
Pit Number |  |  |  | 16mm Earth Cable Terminated From Earth Rod to Earth Bar | [6 empty] | 6mm Earth Cable Installed From Earth Bar to SIT | [9 empty] | SIT Mounting Tray Installed
[7 empty] | INSPECTION AND TEST PLAN - 113a Pit Fit Out | [21 empty] | Page |  |  |  | 1 of 2
[29 empty] | Issue Date |  |  |  | 2024-03-30
[29 empty] | Revision |  |  |  | 1
REPORT DETAILS |  |  | Date Completed | [15 empty] | Drawing References | [9 empty] | ZULU-BECA-024-DWG
|  |  | Project |  |  |  | Taxiway Zulu 2.0 | [11 empty] | Sheet Completed by
Location on Site
WORK DETAILS | [18 empty] | Legend | [9 empty] | ✓ yes ✗ no NA not applicable
PIT PREPARATION | [18 empty] | CABLE TRAY INSTALL | [9 empty] | NOTES
Pit No. |  |  | Pit Size (eg. 1.2m x 1.2m) |  |  |  | New Pit Cleaned? (Y/N) | [5 empty] | Trim Conduit (20mm Above) | [5 empty] | SIT Mounting Tray/Brackets Installed
[7 empty] | INSPECTION AND TEST PLAN - 113a Pit Fit Out | [21 empty] | Page |  |  |  | 2 of 2
[29 empty] | Issue Date |  |  |  | 2024-03-30
[29 empty] | Revision |  |  |  | 1
WORK DETAILS | [18 empty] | Legend | [9 empty] | ✓ yes ✗ no NA not applicable
PIT PREPARATION | [18 empty] | CABLE TRAY INSTALL | [9 empty] | NOTES
Pit No. |  |  | Pit Size (eg. 1.2m x 1.2m) |  |  |  | New Pit Cleaned? (Y/N) | [5 empty] | Trim Conduit (20mm Above) | [5 empty] | SIT Mounting Tray/Brackets Installed