## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP041 - AGL Pit Fit Out | itp |  |  |  |  | FH-ZU2-QU-ITP041 - AGL Pit Fit Out - Rev 0
section | 1.0 - Preliminary Works
checkpoint | 1.1 - Check for Correct Documentation
label | Frequency - Prior to start
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings.
label | – all drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to start
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.3 - Definition of the work area & survey check
label | Frequency - Prior to start
label | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Work area to be clearly defined as per For Construction drawings prior to trenching and install.
label | ○ Ensure excavation permit obtained and (if required) services in work(s) area isolated.
label | Reference Documents - IFC Drawings, Excavation Permit
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | SCP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
section | 2.0 - Installation of SIT Pits
checkpoint | 2.1 - Pit excavation and placement
label | Frequency - Each Lot
label | Acceptance Criteria - Dig zone marked out and excavation undergone in accordance to relevant permit. Pit placed and levelled as per survey set out.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 2.2 - Conduit positioning
label | Frequency - Each Lot
label | Acceptance Criteria - Primary and secondary conduits positioned in pit according to IFC drawings.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.3 - Bedding and backfill of pit surrounds
label | Frequency - Each Lot
label | Acceptance Criteria - Each pit shall be bedded and backfilled with stabilised sand.
label | Reference Documents - ZULU-BECA-001-SPC-00004
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
label | HP*
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 2.4 - Pit number labelling
label | Frequency - Each Lot
label | Acceptance Criteria - Each pit shall be painted with the pit number with black waterproof paint on the inside and top half of the pit wall. Characters shall be 50mm high.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 2.5 - Pit close out
label | Frequency - Each Lot
label | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished.
label | Reference Documents - ZULU-BECA-001-SPC-00004
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
section | 3.0 - Earthing & Fit Out
checkpoint | 3.1 - Earthing & pit fit out
label | Frequency - Each Lot
label | Acceptance Criteria - If no SITs:
label | ○ 16mm Earth Cable Terminated From Earth Rod to Earth Bar
label | If pit houses SIT:
label | ○ 6mm Earth Cable Installed From Earth Bar to SIT, 10 holes to be pre drilled into Earth Bar
label | ○ SIT Mounting Tray Installed
label | ○ SIT installed on the same tray which supply different circuits to have a 300mm gap clearance (Second tray to be provided if 300mm separation cannot be achieved on a single layer)
label | Reference Documents - Drawings, ZULU-BECA-001-SPC-00004
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed ADBSG, Earthing & Pit Fit Out checklist
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: