## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | HPP-UGL-CIV-GN-GEN-ITP-015 FRP (structures) - Rev.2 | itp |  |  |  |  | HPP-UGL-CIV-GN-GEN-ITP-015 FRP (structures) - Rev.2
section | 1.0
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.2 - Lot Traceability
label | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | Acceptance criteria - Prepare a lot map for traceability of the work area.
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.3 - Set out
label | Ref docs - Drawings
label | Acceptance criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.4 - Underlying Lot Conformance
label | Ref docs - Underlying Lot ITP
label | Acceptance criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | ○ Refer underlying lot ITP(s)
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.5 - Site Checklist(s)
label | Acceptance criteria - Have Site checklist(s) been signed and uploaded?
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Site Checklist(S)
section | 2.0
checkpoint | 2.1 - Excavation
label | Acceptance criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
label | ○ Ensure excavation is carried out to a width which will not impede external formwork.
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
checkpoint | 2.2 - Unsuitable Material
label | Ref docs - Spec. 1112 Earthwork s [Cl 4.6]
label | Acceptance criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
label | ○ HOLD POINT
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Compaction - Foundation
label | Ref docs - Spec. 1112 Earthworks [Cl 4.7, 4.13], Spec 0161 [CL 7.2]
label | Acceptance criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 97% modified to a depth of 200mm below foundation level
label | ○ Test Frequency = 1 per 500m2
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 2.4 - Foundation Inspection
label | Ref docs - Spec. 1112 Earthwork s [4.7]
label | Acceptance criteria - Foundation to be inspected by the Superintendent prior to placing blinding
label | ○ HOLD POINT
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.5 - Blinding
label | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
label | Acceptance criteria - Blinding (N15) for Reinforced Concrete Bases to be a 100mm thick mass concrete layer or as otherwise shown on the drawings.
label | ○ Unreinforced bases can be poured directly on the earth
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 2.6 - Mating Concrete Surface Preparation
label | Ref docs - Spec. 0002 [CL 3.9]
label | Acceptance criteria - Construction joints prepared and free of loose material
label | ○ Dowelled joints prepared and bond breaker applied for expansion joints if applicable
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
section | 3.0
checkpoint | 3.1 - Formwork
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.0] Drawings
label | Acceptance criteria - Formwork installed as per drawings and adequately supported.
label | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | ○ Formwork engineers inspection certificate complete and received Survey report to be received prior to ordering concrete.
label | ○ HOLD POINT
label | ○ Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Steel reinforcement
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.0] Drawings
label | Acceptance criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars. Inspection per layer installed.
label | ○ Concrete pre-pour inspection complete.
label | ○ HOLD POINT
label | ○ Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Reinforcement Splice Lengths
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.7]
label | Acceptance criteria - Where splicing of reinforcement is not shown on drawings min. lap lengths shown below shall be adopted. (SPT-0002 Table 6)
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.4 - Pit & Pipe Connections
label | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3], Spec. 0002 Concrete supply, construction, and grouting [Cl 2.6] Drawings
label | Acceptance criteria - Inlet and outlet pipes to be integrally cast into foundation/pit walls and the joint waterproofed as per design requirements.
label | ○ Embedded pipes to be adequately restrained against flotation
label | ○ HOLD POINT
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - ITP for associated pit/pipe reviewed for conformance
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Installation of Core Holes, Voids, HD Bolts and Embedments
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
label | Acceptance criteria - Firmly Fixed in position in all directions
label | ○ Reinforcement displaced where necessary, bars requiring cutting approved by superintendent
label | ○ Integrity of surface treatments maintained (galvanising, painting etc) Threads covered
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.6 - Tolerances of Core Holes, HD Bolts and Embedments
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
label | Acceptance criteria - HD bolts positioned using a template. Tolerance for HD bolts as per CL 7.2 (see below table)
label | – – – – – – – – – – – – – – – –
label | Condition ¦¦ Tolerance
label | – – – – – – – – – – – – – – – –
label | Any 2 bolts within a group ¦¦ ± 3mm Centre to Centre
label | Adjacent HD bolt groups ¦¦ ± 6mm Centre to Centre
label | Bolt Projections – From concrete level ¦¦ + 5mm, -0mm
label | Embedded steel finishing flush with surface ¦¦ ± 3mm from surface
label | Bolt reduced level ¦¦ + 5mm, -0mm
label | Verticality of any bolt ¦¦ 1:300
label | – – – – – – – – – – – – – – – –
label | Maximum accumulation of 6 mm per 30,000mm along an established column line of multiple HD bolt groups, but not to exceed a total of 25 mm.
label | 6 mm from the centre of any HD bolt group to the established column line through that group.
label | – – – – – – – – – – – – – – – –
label | * Before pouring concrete of the GT & GEN foundation, MPW TA will check the setting condition of GT & GEN anchor bolt. Witness Point as per MHI ITP.
label | ○ Tolerances for other embedded fabricated items in line with AS 3990 or AS4100 as applicable.
label | ○ Pre-pour survey performed and recorded to verify location
label | ○ HOLD POINT
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection and Survey Records Inc MHI Check Sheet for GT & GTG Anchor Bolt Setting CG-64294
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - Earthing for Concrete Structures
label | Ref docs - Drawings Spec. 0002 Concrete supply, construction, and grouting [CL 2.6]
label | Acceptance criteria - Earthing installed for concrete structures as per provided Drawings
label | ○ HOLD POINT
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | UGL Earthing FIC
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.8 - Concrete Mix and properties
label | Acceptance criteria -
textbox | Concrete compressive strength required (28 days) |  |  | MPA
textbox | Approved Concrete mix ID
textbox | Slump |  |  | mm
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material dockets
bool | Concrete pour records
checkpoint | 3.9a - Concrete Supply Temperature - GT Foundation Only
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2] Thermal Analysis Report
label | Acceptance criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 25°C.
label | ○ Ambient air temperature at the time of placement must be between 5oC and 30oC.
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material dockets
bool | Concrete pour records
checkpoint | 3.9b - Concrete Supply Temperature - Other foundations
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2]
label | Acceptance criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 30°C.
label | ○ Ambient air temperature at the time of placement must be between 5oC and 32oC.
label | ○ If ambient temperature is between 32oC and 38oC, seek approval from superintendent to proceed by taking special precautions noted in the specification.
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material dockets
bool | Concrete pour records
checkpoint | 3.10 - Concrete Placement
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.4]
label | Acceptance criteria - Ensure elapsed time between batching and discharge of the mix does not exceed 1.5 hours.
label | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
label | ○ Concrete thoroughly compacted – one internal vibrator per 10m3 concrete placed per hour
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material dockets
bool | Concrete pour records
checkpoint | 3.11 - Concrete Slump Testing
label | Acceptance criteria - Slump Test - One per batch of concrete
label | ○ Slump within tolerances specified in AS 1379
label | – – – – – – – – – – – – – – – –
label | TABLE 5.1 PERMISSIBLE TOLERANCE ON SLUMP
label | – – – – – – – – – – – – – – – –
label | Specified slump, mm ¦¦ Tolerance, mm
label | <60 ¦¦ ±10
label | ≥60 ≤80 ¦¦ ±15
label | >80 ≤110 ¦¦ ±20
label | >110 ≤150 ¦¦ ±30
label | >150 ¦¦ ±40
label | – – – – – – – – – – – – – – – –
label | ○ Testing to be executed by a NATA accredited test facility
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete pour record
checkpoint | 3.12 - Concrete Compressive Strength Testing
label | Ref docs - Drawings
label | Acceptance criteria - Compressive Strength Testing - 2 x 7day and 2 x 28day per 50m3
label | ○ Testing to be executed by a NATA accredited test facility
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete pour record
checkpoint | 3.13 - Surface finish
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2] Drawings
label | Acceptance criteria - Concrete surfaces shall be true and even, free from honeycombed surface depressions or rejections.
label | ○ Formed surfaces conform with surface finish requirements of AS3610 for the surface class nominated.
label | ○ WITNESS POINT
label | ○ 1 day prior
button | Acceptance | Yes,No,N/A
label | HPP CON Key - W
label | HPP QA Key - W
checkpoint | 3.14 - Surface Treatments
label | Acceptance criteria - Any surface treatments to be applied are approved for use and appropriate dose rates have been determined
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.15 - Joints
label | Ref docs - As per drawings
label | Acceptance criteria - As per design drawings. Sawn joints to commence as soon as the concrete has hardened sufficiently.
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.16 - Curing
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
label | Acceptance criteria - From completion of finishing cure continuously with an approved method for a min period of 7 days or as directed by the Superintendent.
label | a. Ordinary Portland cement concrete – 7 days
label | b. High early strength concrete – 3 days
label | c. Concrete with cement or pozzolan materials – 10 days
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.17 - Stripping of formwork
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.4.5]
label | Acceptance criteria -
label | – – – – – – – – – – – – – – – –
label | Member Type ¦¦ Member ¦¦ *Effective Span mm ¦¦ Minimum Stripping Time (days) for Average Air Temperature during period prior to Stripping
label | – – – – – – – – – – – – – – – –
label | - ¦¦ - ¦¦ - ¦¦ 20°C and over ¦¦ 10°C to 20°C ¦¦ 4°C to 10°C ¦¦ Under 4°C
label | Vertical Unloaded ¦¦ Wall, column, beam side, slab side ¦¦ 0 ¦¦ 2 ¦¦ 3¦¦ 5 ¦¦7
label | Vertical Loadbearing ¦¦ Wall, column Or loadbearing structure ¦¦ 0 ¦¦ 5 ¦¦ 6 ¦¦ 7 ¦¦ 9
label | Horizonal ¦¦ Slab ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 7, 10, 14 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28
label | Horizontal ¦¦ Beam ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28 ¦¦ 28, 28, 28
label | – – – – – – – – – – – – – – – –
label | * Effective span is the maximum distance between supports (either temporary or permanent)
button | Acceptance | Yes,No,N/A
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.18 - Concrete Repair (If required)
label | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.7]
label | Acceptance criteria - Defective concrete shall be repaired or replaced. The materials and techniques of repair shall be examined and approved by the Superintendent prior to the commencement of repairs.
button | Acceptance | Yes,No,N/A
label | HPP CON Key - H
label | HPP QA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Grout Placement Checklist
bool | Approved Aconex Corro for Repair Methodology
holdpoint | AUTHORITY HOLDPOINT
section | 4.0 Backfill and Compaction
checkpoint | 4.1 - Structure Backfill
label | Ref docs - Spec. 1112 Earthworks [Cl 4.10]
label | Acceptance criteria - Backfill to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
label | ○ Placed in layers of maximum compacted thickness of 150mm
label | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Test Report
checkpoint | 4.2 - Compaction - Backfill
label | Ref docs - Spec. 1112 Earthworks [Cl 4.13]
label | Acceptance criteria - Minimum relative compaction requirements for backfill against structures to be:
label | – 92% for general fill
label | – 97% for select fill
label | ○ Test Frequency = 1 per layer
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 4.3 - Moisture Content
label | Ref docs - Spec. 1112 Earthworks [Cl 4.13 & 7.1]
label | Acceptance criteria - Moisture Content for Backfill material to be within 60% to 90% OMC unless otherwise approved by Superintendent
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
section | 5.0 Conformance check
checkpoint | 5.1 - Survey Report
label | Ref docs - Spec. 0161 Quality [Cl 3.13] AS3610
label | Acceptance criteria - An as-built survey of the structure has been completed to ensure all structures are within the following construction tolerances:
label | ○ Absolute position in plan shall be within 10 mm.
label | ○ Floor to floor plumb shall not exceed 0.002 times the dimension between the floors or 10 mm whichever is the greater.
label | ○ Deviation from the specified dimension shall not exceed 0.001 times the specified dimension or 5mm, whichever is the greater.
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - H
label | HPP QA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Concrete Test Results
label | Ref docs - Spec. 0002 [Cl 8.2]
label | Acceptance criteria - Certificates received, reviewed and conforming to requirements for each pour.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 5.3 - Acceptance and closure of non-conforming items
label | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | ○ HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - H
label | HPP QA Key - H
holdpoint | AUTHORITY HOLDPOINT