## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP/R Test Report Pre-Action System (V.260521) |  |  |  |  | Yes | ITP/R Test Report Pre-Action System (V.260521) | 0b35b2ef-d2cd-4e45-a553-3aacaa9de57b
checkpoint-group |  |  | section | Installation Testing
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 844133e1-871d-52b9-9d9c-32bfa558ff44 |  | textbox | Drawing & Revision #
boolean | c38cc06b-4b78-5dac-ba2c-3f3aad3791fc |  | tickbox | Area clear, tidy and accessible
label | bb2d8abc-584e-5a44-aaad-6155d904c901 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
label | 38886f8a-c065-5528-b142-28785172315f |  | note | Acceptance Criteria: Installed to Approved Drawings
checkpoint-status |  |  | checkpoint | Installation inspection of trunk mains and range pipes
label | e1e2f940-7c79-55da-8172-cc614c2d3e6e |  | note | Acceptance Criteria: Installed to Approved Drawings
checkpoint-status |  |  | checkpoint | All dirt traps must be capped and all pops temporarily plugged
label | 3cf273de-5bd1-5447-ae9c-4eb8eabfe8b1 |  | note | Acceptance Criteria: Installed to Approved Drawings
checkpoint-status |  |  | checkpoint | Inspection of installed sprinkler heads & baffle plates and flexible droppers
label | 03208669-ef9f-5f19-941d-06c5d48ce641 |  | note | Acceptance Criteria: Installed to A.S 2118.1
checkpoint-status |  |  | checkpoint | Perform Pneumatic leak test of pipework to ensure no loose joints or open pipe ends
label | 04ad91d3-2786-52c3-9224-de413b86db00 |  | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
checkpoint-status |  |  | checkpoint | Perform Hydrostatic Testing of pipework. Gradually apply pressure increments of 500 kPa for 15 minute holds until test pressure of 1400 kPa or 400 kPa above maximum static working pressure of the system is achieved and hold for 2-hours
label | 462c1fee-beba-50f7-ae5d-6653beee28b6 |  | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 7.9.4
checkpoint-group |  |  | section | Installation of Pre-Action Valve Sets & Ancillary Equipment
checkpoint-status |  |  | checkpoint | Installation inspection of pre-action valve sets and ancillary equipment to ensure completeness, correct location, mounting
label | 266bfe91-646f-5a78-9c3f-12dc83cd22c3 |  | note | Acceptance Criteria: AS 2118.1-1999 Clause 8.1
checkpoint-status |  |  | checkpoint | Verify installation of alarm devices (e.g. DBA pressure/flow switch, low pressure switch) and solenoid valve for correct type and rating and proper interface connections to Fire Indicator Panel (FIP)
label | 2969bb73-a1f2-53f4-866f-b3d19633b7da |  | note | Acceptance Criteria: Refer AS 2118.1-1999 Clause 8.10.1
checkpoint-group |  |  | section | System Commissioning
checkpoint-status |  |  | checkpoint | Perform a trip test on each pre-action valve by opening the alarm test ball valve and check operation of water motor alarm. Confirm operation of DBA pressure switch with correct indication at fire indicator panel
label | 53aa6cf2-4942-5001-bb0e-816e85d86493 |  | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, DBA -3 mins
checkpoint-status |  |  | checkpoint | Initiate single or double interlock release activation and check operation of water motor alarm, DBA pressure switch and correct indication at fire indicator panel
label | b3b2b578-4e01-5610-8d7e-abfb49faeaca |  | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, operational confrimation
checkpoint-status |  |  | checkpoint | Record cut-in / cut-out pressure of air supply compressor and time to recharge the system pressure
label | 8d13ae0d-2149-5847-9d52-fdbb9108a410 |  | note | Acceptance Criteria: Refer AS 2118.1-2006 Clause 15.4b, Time to recharge 30 mins
checkpoint-status |  |  | checkpoint | Reinstate system and ensure valves are secured in its intended position, alarm and monitoring devices are in operational mode and system in ready to operate condition
label | 9f01d373-0f6e-5f02-bc77-1c6ff9035e2c |  | note | Acceptance Criteria: AS 2118.1-2006Clause 15.6
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | a2dfd634-dbf3-57c8-9472-610c95428b57 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 481ec145-987c-596f-89ad-62c19ee25ddc |  | button | Area left clean & tidy | Yes, No
boolean | 5288f8ea-689d-5b0f-bfee-44bc576c23a6 |  | tickbox | Leemark Sign-Off
boolean | beef6ff2-2bfc-54e8-b6c4-9250f968e97e |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.2 Hydrant Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.2 Hydrant Installation | 11edbfbd-5a6b-41ae-aa3f-ba00451f4f79
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 02836c52-09c8-5c51-9252-7052718375fc |  | textbox | Drawing & Revision #
boolean | e3be11f9-3f05-5650-9339-bc0fba34f619 |  | tickbox | Area clear, tidy and accessible
label | dce5cf10-4230-5eb2-9056-a2d34faac161 |  | note | Attach Photos/Comments below if any issues & send report to Builder
text | 1ad3203c-61c9-5fae-a7d7-5da7f3057231 |  | textbox | Hydrant No.
checkpoint-status |  |  | checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
checkpoint-status |  |  | checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
checkpoint-status |  |  | checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
checkpoint-status |  |  | checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
checkpoint-status |  |  | checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
checkpoint-status |  |  | checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
checkpoint-status |  |  | checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
checkpoint-status |  |  | checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | e01fb01c-c042-5433-a8bf-95d451e06f43 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | ca56816e-9d37-5cd0-8703-3fa3ee435f46 |  | button | Area left clean & tidy | Yes, No
boolean | 98aeee9f-2007-5d2a-b890-5d8d62104ee4 |  | tickbox | Leemark Sign-Off
boolean | f2abb84a-14cc-5091-97b3-09fbf91110a1 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.1 Fire Pump Installation | 14f76abe-ed65-48ab-9fba-ca85311be7ba
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 68fde230-243c-537c-8674-e1f0cf2f7728 |  | textbox | Drawing & Revision #
boolean | 06a227f9-1904-5154-a47c-81aababb569d |  | tickbox | Area clear, tidy and accessible
label | 2a7a22d9-f784-5e76-bea9-7d748632a35f |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
checkpoint-status |  |  | checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
checkpoint-status |  |  | checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
checkpoint-status |  |  | checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
checkpoint-status |  |  | checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
checkpoint-status |  |  | checkpoint | Suction isolation valve installed is OS & Y type
checkpoint-status |  |  | checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
checkpoint-status |  |  | checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
checkpoint-status |  |  | checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
checkpoint-status |  |  | checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
checkpoint-status |  |  | checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
checkpoint-status |  |  | checkpoint | Exhaust connected to pump and installed to approved discharge location
checkpoint-status |  |  | checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 5a32277a-53ad-53cb-9c33-e0e0118cd388 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 20d27302-39f3-5f67-b923-0ea69e0ca039 |  | button | Area left clean & tidy | Yes, No
boolean | 06b24c80-4baf-5533-a858-e452e2f8688e |  | tickbox | Leemark Sign-Off
boolean | 881f36f4-f586-5eea-afb5-2c5891efcf60 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | Handover ITP (V.200521) |  |  |  |  | Yes | Handover ITP (V.200521) | 18e73c35-f490-4399-ad6b-3567c9f22d3c
checkpoint-group |  |  | section | Design
checkpoint-status |  |  | checkpoint | Shop Drawings - Pass once completed
label | 8e21ed16-657f-5808-9a2f-13421c82ad58 |  | note | By: Drawing Office
label | 28b99707-a4b3-587d-9d0a-b305861ce9e4 |  | note | Verification Criteria
label | f6b85a84-ae1b-5766-9d5e-90c7c935e409 |  | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
label | fb3877ea-9760-5cbd-bb00-03f6d16cefc1 |  | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
label | d077a0d0-f94d-51cd-bc95-e266cf3b51f1 |  | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
label | 211256e5-5e05-5cbb-8454-2e2cdf12c3ca |  | note | AS2441-2005 Installation of Hosereels
label | 5ddbcbdd-12d6-5883-bf61-1bd90a87116a |  | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
label | 58eefbad-460d-5c85-b4e9-07ac3e989c0d |  | note | AS 1670.1-2004 Fire detection, warning, control and intercom systems - System design, installation and commissioning
label | a4aa7c01-3d8d-5b30-9751-bc34b265b61b |  | note | AS 1670.4-2015 Fire detection warning control and intercom systems - System design installation and commissioning
label | 5e436985-e0a4-5be1-8e2a-0dd78a6c9701 |  | note | Project specification (TBC - Once known comment below)
label | efdb4b77-cd10-53a7-bc5d-86e1505edb60 |  | note | .. ..
label | d68be9a8-07f2-5eee-aca9-17543b662a85 |  | note | Quality Control Method
button | 7a7eadf7-0236-5e3e-b01f-d71ab706495f |  | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
button | d3581721-4c25-5383-88fd-0956f24d1e1f |  | button | Approved by Project Manager | Yes, No, N/A
button | a87ccb3b-5773-5136-ab38-4c0ffd1b9204 |  | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
label | 552d7f8f-0dcf-5220-a750-2122a72ddb15 |  | note | Records: Aconex
checkpoint-status |  |  | checkpoint | Hydraulic Calculations - Pass once completed
label | 3b732027-3d2d-57a6-a8ba-f40e942ed527 |  | note | By: Drawing Office
label | d789e3fb-d86a-5672-aaf2-c26652dd6ebd |  | note | Verification Criteria
label | 9bd24c06-00df-55c5-9371-e83b6de1ed25 |  | note | AS2118.1-1999 Automatic fire sprinkler systems - Part 1: General Requirements
label | 9471a8f0-01ed-5473-a879-88901371b10f |  | note | AS2118.6-2012 Automatic fire sprinkler systems - Part 6: Combined sprinkler and hydrant systems in multistorey buildings
label | 16ce0911-6e4b-5b16-b614-3971656d6f06 |  | note | AS2419.1-2005 Fire Hydrant Installations - Part 1: System design, installation and commissioning
label | f5674146-a754-5202-962e-d9cc6e96a323 |  | note | AS2441-2005 Installation of Hosereels
label | 6a6146a3-65d4-591f-bf20-bd8787a8ab41 |  | note | AS2941-2013 Fixed fire protection installations – Pumpset systems
label | c0b4cf60-49f3-5b0c-bad8-7eb37b206ea2 |  | note | Latest revision FER. (TBC - Once known comment below)
label | c8073585-e0d6-5387-8e12-80815a83f27b |  | note | Project specification. (TBC - Once known comment below)
label | 843c58b3-b3d3-5a7c-bd63-53992a052973 |  | note | Quality Control Method
button | 333fead2-b9db-5d2d-addb-c9040544d004 |  | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
button | f660ea01-0d4d-5d04-8362-b2aa3f66e157 |  | button | Approved by Project Manager | Yes, No, N/A
button | 6cd29afd-07c7-57c1-9ea6-e37174e27763 |  | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
label | 6a42ca05-52cd-560c-b588-b0ed59818902 |  | note | Records: Aconex
checkpoint-status |  |  | checkpoint | Samples - Pass once completed
label | 7a4c57e4-8827-547a-9f87-9d4ab95479e2 |  | note | By: Drawing Office
label | 65ee3464-7a5d-59fa-90f1-8809f3ac97f9 |  | note | Verification Criteria: Part C.1 Samples & Details Part C.8 Fire Sprinkler System Part C.9 Fire Hydrant Pipe
label | 742055d2-08d3-5256-a7ec-0c149cac637f |  | note | Quality Control Method
button | b7095eb4-2176-57eb-a042-6870088b4122 |  | button | HOLD POINT - Leemark add signature below | Yes, No, N/A
button | 1d64f07c-422e-5c72-8fd4-aa7e32b8f2ad |  | button | Approved by Project Manager | Yes, No, N/A
button | 751bf811-12f9-52a1-af17-86cba1ed4909 |  | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
label | f0a98a23-19ab-58f3-9db1-db1f04b98d7d |  | note | Records: Aconex
checkpoint-group |  |  | section | Offsite Manufacture
checkpoint-status |  |  | checkpoint | Pipework Fabrication - Pass once completed
label | 18b0f321-bd67-57aa-a437-f6e21cc57721 |  | note | By: CWS
label | e35a2910-2f84-55aa-b9e4-4a161122163e |  | note | Verification Criteria: C.12 Pipework & Fittings
label | fe78dcfb-38de-515c-830c-6c3677a93f09 |  | note | Quality Control Method
button | b29069a1-5806-5656-957a-89d0c26dafa8 |  | button | Leemark Inspection Completed | Yes, No, N/A
label | 5f543120-8fbd-506d-a6e3-3e745d2a3d95 |  | note | Records: CWS/ITR
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Sprinkler - Pass once completed
label | 1c56aecc-a6e8-5ee8-a9a7-ef8a0264e2a4 |  | note | By: Sprinkler Fitters
label | a37fd250-e671-5161-90aa-ffb57684311d |  | note | Verification Criteria: Part C.8 Fire Sprinkler System AS2118, 4118
label | 16c3ecd9-9cff-5079-b0cb-fd963329c54b |  | note | Quality Control Method
button | b37d257a-b773-56a0-872e-e90b408e5eb9 |  | button | Leemark Inspection Completed | Yes, No, N/A
button | 2ed5abf4-f895-523e-8a1f-b55a22853a97 |  | button | Witnessed by Project Manager | Yes, No, N/A
label | 241fe270-051b-509b-b53e-bcd78008c049 |  | note | Records: Inspection & Test Record, 301/301.1 & 301.2
checkpoint-status |  |  | checkpoint | Hydrant & hose Reels - Pass once completed
label | 19230c38-871a-5008-9546-51b901d84191 |  | note | By: Sprinkler Fitters
label | 50aca357-c828-5c05-b65a-d667bcb5f52e |  | note | Verification Criteria: Part C.9 Fire Hydrant Pipe & Hose Reel Installations AS2419.1/.2/.3 & 2441
label | 5ff5129d-708f-565f-bf14-47edfe5b4c04 |  | note | Quality Control Method
button | a90ebfb4-63f8-56fa-913c-373984ee03aa |  | button | Leemark Inspection Completed | Yes, No, N/A
button | ff9469c9-6a09-57e6-8534-faa0e110e069 |  | button | Witnessed by Project Manager | Yes, No, N/A
label | 4826fd02-592c-5945-95ae-62afc80884ee |  | note | Records: Inspection & Test Record, 302.2/302.3 & 302.4
checkpoint-status |  |  | checkpoint | Alarms / EWIS - Pass once completed
label | fa104792-de17-57a5-ae83-ba1d0ffce0c3 |  | note | By: Fire Alarm Technicians
label | 31d71fa6-c976-59e8-847e-a04cf5cde391 |  | note | Verification Criteria: Part B.12 Fire Detection & Alarm Installation, Part B.13 Emergency Warning & Intercommunication System AS1670
label | 4698edf5-59e5-5e23-9d92-86dbc7bda5c7 |  | note | Quality Control Method
button | e1dcdcbd-46ad-5b23-8749-9f646a89c12e |  | button | Leemark Inspection Completed | Yes, No, N/A
button | 485d7468-674a-5fea-894d-4834f02a1b71 |  | button | Witnessed by Project Manager | Yes, No, N/A
label | d658b17d-2dd9-5c3d-8e63-20f0a1329f6c |  | note | Records: Inspection & Test Record, 303.1 / 303.2 / 303.3 / 303.4 / 303.5
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Hydrostatic Tests - Pass once completed
label | 0bd86e47-5d8d-5980-ae1d-40c6c9797613 |  | note | By: Sprinkler Fitters
label | e33fceaf-6b67-5b77-84ee-e14899539ec1 |  | note | Verification Criteria: AS2118, 4118, 2419, 2441, 2941
label | 3ab15ca4-7bf5-5cfb-a7dc-d6ec364d4e09 |  | note | Quality Control Method
button | 370a6403-895b-51e9-86ae-095fbbe28f5f |  | button | Leemark Inspection Completed | Yes, No, N/A
button | d70dee45-343a-5f4c-8577-a363bc678c7f |  | button | Witnessed by Project Manager | Yes, No, N/A
label | a54bff67-684d-5d19-9295-10d96af0b889 |  | note | Records: Inspection & Test Record, 401
checkpoint-status |  |  | checkpoint | Sprinkler Inspection - Pass once completed
label | 87a429a0-e143-5c8e-9b50-849da90636da |  | note | By: Fire Safety Victoria
label | c7aaae11-5559-5256-a13f-0b51a54d2f59 |  | note | Verification Criteria: AS2118.1, AS2118.6
label | ebc353e6-4a18-56d1-bfec-3ae52a45bb0c |  | note | Quality Control Method
button | 32149feb-02d1-5f1d-93f4-84ff3c6a5373 |  | button | Witnessed by Project Manager | Yes, No, N/A
label | 63fbe6e7-9ee0-5dc3-a900-1d26e41895ce |  | note | Records: Certificate issued - Attached below as applicable
checkpoint-status |  |  | checkpoint | Hydrant Inspection - Pass once completed
label | 4e5520e0-8737-5ea4-8831-0f8404823ba2 |  | note | By: Victorian Hydrant Test & Plumbing
label | b574b2ab-65af-5054-909d-2c4c074fdeaa |  | note | Verification Criteria: AS2419, AS2118.6
label | 26ccbada-d706-5ce4-908b-6991163c3e10 |  | note | Quality Control Method
button | c15638e3-3311-572f-88c1-bafe2716c186 |  | button | Witnessed by Project Manager | Yes, No, N/A
label | 465ecdf7-3360-55ba-aa6b-095892e7c9c5 |  | note | Records: Certificate issued - Attached below as applicable
checkpoint-status |  |  | checkpoint | Alarms / EWIS Inspection - Pass once completed
label | 0662f9ec-7cb7-5708-87ad-5d720cbe4f1d |  | note | By: Fire Safety Victoria
label | 0890b115-7270-5c9f-bf30-f48791ee9f3d |  | note | Verification Criteria: AS1670
label | d8877a42-1341-5694-a9b4-23a74d09f4d5 |  | note | Quality Control Method
button | 06adcd4a-9629-5422-95a1-07cff1f00c03 |  | button | Witnessed by Project Manager | Yes, No, N/A
label | 902eba8e-4707-5bb9-ad7f-42c00bd7c7ee |  | note | Records: Certificate issued - Attached below as applicable
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | As Installed drawings - Pass once completed
label | 607fdf1d-8c12-5e15-9d63-4f70f007bb5d |  | note | By: Drawing Office
label | 6c36bd21-564e-507d-afab-4ea75e3fbdde |  | note | Verification Criteria: AS2118.1, AS2118.6, AS1670
label | 63736753-55a5-502a-acdd-1e7e2b7a5dc4 |  | note | Quality Control Method
button | 8aaa2b52-7d0c-501b-ba53-8b4641f07720 |  | button | Document Submitted by Leemark | Yes, No, N/A
button | 67232538-6f08-59c6-a148-8b432945680b |  | button | Approved by Project Manager | Yes, No, N/A
button | f9092ec3-8f25-5db2-a647-3d9a9a27050d |  | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
label | a02c682b-12dc-5f37-ac81-95afa517d633 |  | note | Records: Operation & Maintenance Manual - Attached below as applicable
checkpoint-status |  |  | checkpoint | Manuals - Pass once completed
label | b7066152-a2f3-5428-a732-3a136e51c0dd |  | note | By: Drawing Office
label | 7e47c988-f492-5d83-bb74-dff9f900fae4 |  | note | Verification Criteria: As per SOW
label | e2d81918-4ca4-5303-8550-7e6702ec2935 |  | note | Quality Control Method
button | 34c275e8-7a02-59bd-a4ca-b4c378160c6e |  | button | Document Submitted by Leemark | Yes, No, N/A
button | 2d41cd87-85cb-5bdd-9ec5-9100891f0a75 |  | button | Approved by Project Manager | Yes, No, N/A
button | d0905132-a5d6-5673-bbc5-f8c2003ea3b7 |  | button | Approved by Fire Services Engineer/Builder | Yes, No, N/A
label | 3af63e93-ca29-5aa8-9856-a4818fc27076 |  | note | Records: Operation & Maintenance Manual - Attached below as applicable
checkpoint-status |  |  | checkpoint | Test Data - Pass once completed
label | cb5ecc93-db21-590f-8120-aec4daf10569 |  | note | By: Site Foreman
label | b67e3f3f-f859-590b-b8ea-a4b3eb806ebd |  | note | Verification Criteria: Refer Commissioning part of this plan
label | d562f040-4326-51b0-8d1a-de482abddb3f |  | note | Records: Operation & Maintenance Manual - Attached below as applicable
checklist-sectioned |  |  | checklist | ITP/R Test Report Gaseous Suppression System (V.240521) |  |  |  |  | Yes | ITP/R Test Report Gaseous Suppression System (V.240521) | 1a1b82a2-3ef1-424a-a466-407405edf90f
checkpoint-group |  |  | section | Installation Testing
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 5b57104a-56ba-51d5-b12e-af6d3a39ab81 |  | textbox | Drawing & Revision #
boolean | 12aaa62d-0712-5e8a-a640-edbbf967e0dc |  | tickbox | Area clear, tidy and accessible
label | 23252166-ad43-598c-8da1-5691b7e8cfc0 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Verify correct type, spacing and elevation of installed pipe supports and hangers
label | 3435241f-b220-59d2-aadf-6585efaed6a5 |  | note | Acceptance Criteria: Installed to Approved Drawings
checkpoint-status |  |  | checkpoint | Installation inspection of pipes and nozzle droppers/risers
label | 542d335f-8de6-539e-a048-28fd509f974b |  | note | Acceptance Criteria: Installed to Approved Drawings
checkpoint-status |  |  | checkpoint | All dirt traps must be capped and all pops temporarily plugged
label | 1843a944-d0a3-53e9-a4de-9e4003b16833 |  | note | Acceptance Criteria: Installed to Approved Drawings
checkpoint-status |  |  | checkpoint | Perform Pneumatic leak test of pipework in accordance with approved Test procedure and SWMS. Gradually apply pressure increments of 100 kPa for 15 minute holds
label | 75c9d4e2-45a2-58b5-aa09-5c915b126a43 |  | note | Acceptance Criteria: Pressure drop should not exceed 20% of 300 kPa for 10-mins
checkpoint-group |  |  | section | Installation of Cylinders, Manifolds, Valves, Actuation, Discharge Hoses & Nozzles
checkpoint-status |  |  | checkpoint | Cycinders shall be adequately mounted and suitably supported according to approved installation plan
label | aa22c2ae-93a6-5d24-bc9f-44e5f0be8676 |  | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 8.2.3.12a
checkpoint-status |  |  | checkpoint | Discharge manifolds and valves shall be mounted and adequately supported
label | e8534040-8f74-5e49-959f-e12e987a0479 |  | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.4
checkpoint-status |  |  | checkpoint | Adequate quantity, correct code and location of discharge nozzles shall be installed according to approved plan
label | b97526e1-822a-54d6-aed0-3285e90debd4 |  | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.3.6.1
checkpoint-status |  |  | checkpoint | Detection, actuation, alarm and control systems shall be installed and tested by “DRY FIRE” contractor in accordance to relevant code/standards
label | 39174192-d228-595d-a30d-cd9d126f605e |  | note | Acceptance Criteria: Installed to Approved Drawings, AS 14520.1-2009 Clause 6.4.1
checkpoint-group |  |  | section | Enclosure Integrity Pre-Test Inspection
checkpoint-status |  |  | checkpoint | Client to confirm that all services penetrations and/or openings are sealed prior to the test
label | 6f5c9a97-2e78-51c4-ae8d-3cf28109ef09 |  | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
checkpoint-status |  |  | checkpoint | Client to confirm that all HVAC fire rated dampers including OPR Damper can be closed prior to the test
label | aa7eb933-acac-5091-9a4f-b6e4269e891b |  | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
checkpoint-group |  |  | section | Enclosure Integrity Test
checkpoint-status |  |  | checkpoint | Perform both pressurization and depressurization fan test of the room and using the software program, confirm that holding time is equal or more than the required 10 minutes
label | 8ce1445d-1196-5a03-b031-0a786432012e |  | note | Acceptance Criteria: Relief Damper Installed is sufficient
checkpoint-status |  |  | checkpoint | Prepare full test report of each enclosure demonstrating the level of compliance achieved
label | 72652afe-e74e-5d90-bd70-a9c9b4affce8 |  | note | Enclosure PASSED the hold time & venting requirements
checkpoint-group |  |  | section | System Commissioning and Acceptance
checkpoint-status |  |  | checkpoint | Prior to start of any test, ensure all extinguishant storage container release mechanism are disabled or removed
label | a0e7bfe8-c841-553b-af8a-7aea46ce4a73 |  | note | Acceptance Criteria: Release Mechanism Isolated
checkpoint-status |  |  | checkpoint | Verify and confirm compliance to the approved design of distribution piping system, discharge nozzle sizes & orientations, storage containers quantity & locations and warning signs & notices locations
label | be2e11ae-6ff3-5f4b-b4b8-d07a8dbd058b |  | note | Acceptance Criteria: Installed to Approved Drawings
checkpoint-status |  |  | checkpoint | With the operation of fire alarm system, verify and confirm operation of audible & visual alarms, plant shutdown interface, time delay & release mechanism activation/30s time delay / solenoid operated/ audible visual Alarm
label | fcea09e4-5a0c-5833-a116-97177ea97a74 |  | note | Acceptance Criteria: 30s time delay, solenoid operated , Audible/visual alarm operated
checkpoint-status |  |  | checkpoint | Simulate discharge pressure switch operation and confirm gas released alarm indication at Fire Suppression Panel
label | 1f8c18df-932c-5b59-b8e3-5fa748928795 |  | note | Acceptance Criteria: Indication at FIP
checkpoint-status |  |  | checkpoint | After completion of system functional test, reset and reconnect all release mechanism onto storage container and return the system to full service condition
label | a53b1919-079c-5258-b7ce-ff36c88ff5b5 |  | note | Acceptance Criteria: Builder Approval (Click to add signature Sign-Off below as required)
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | f4684c11-06d7-5996-beba-eb3b991d6f3c |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 438736fc-6c03-5609-981a-307ed92d542f |  | button | Area left clean & tidy | Yes, No
boolean | c67616bc-ad4e-5162-a6f0-0c309b2170ed |  | tickbox | Leemark Sign-Off
boolean | e5c9317c-7180-57ff-a410-52bceb7f086f |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve |  |  |  |  | Yes | LM-FOR-30-ITR-301.1 Sprinkler Control Valve | 1a750fe7-8faf-48fb-a5bd-5632afd266f8
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 7752cb60-a124-551a-a7ac-19d9568cab87 |  | textbox | Drawing & Revision #
boolean | 7dd50159-d911-53e6-badd-b4156cbf63ff |  | tickbox | Area clear, tidy and accessible
label | d28385b1-50e7-57ca-a400-fb8a660ec2e6 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
checkpoint-status |  |  | checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint-status |  |  | checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
checkpoint-status |  |  | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint-status |  |  | checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | Correct type solenoid, flow switch, couplings etc installed
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
checkpoint-status |  |  | checkpoint | Control Valve is positioned between 1150mm to 1800mm
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | e2c7e4c7-70a1-5ae6-87a9-ad92bf954ad0 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | fd6d1d3e-bdc8-545d-be3e-d652326d29a2 |  | button | Area left clean & tidy | Yes, No
boolean | 6986d8ad-fdc1-592f-880c-8f7604e857a6 |  | tickbox | Leemark Sign-Off
boolean | 3734b0b8-2706-5b5f-a2ac-1f15f98ad771 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off |  |  |  |  | Yes | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off | 2fa5fde8-7a5d-45b1-8816-3f8273ddbd91
checkpoint-group |  |  | section | EWIS Fit-Off
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 0dd0ac1a-bea0-50ad-bb01-0f580c3876d6 |  | textbox | Drawing & Revision #
boolean | 111ab4be-2fa4-5a91-a0f1-b81e2f35ec2b |  | tickbox | Area clear, tidy and accessible
label | 6eb6f44c-2170-5eb9-a0ae-222b7c8ddb89 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all speakers / horns been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all warden intercom points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all emergency call points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all strobes been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all background music points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all microphone points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
checkpoint-status |  |  | checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all devices been terminated for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been connected to the first device
checkpoint-status |  |  | checkpoint | Have all end of lines been fitted and measured
checkpoint-status |  |  | checkpoint | Have cables feeds been connected at the panel
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
checkpoint-status |  |  | checkpoint | Check that no cables or devices have been damaged
checkpoint-status |  |  | checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | b99276a5-db2b-56d0-84c9-a0266316a561 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 206fbff5-aa06-5468-bc71-f8c57a79dfd1 |  | button | Area left clean & tidy | Yes, No
boolean | d2904f5b-a547-5ea2-b8b4-b4f5730caa38 |  | tickbox | Leemark Sign-Off
boolean | 0f79fc8b-cd9c-59fa-83e5-cd670db59be5 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test |  |  |  |  | Yes | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test | 486ab86b-f5cb-401f-9122-27fff2b70ad0
checkpoint-group |  |  | section | Guidelines
checkpoint-status |  |  | checkpoint | Guidelines understood - Pass once read
label | ab4a5186-9d30-54cd-a77f-853ce47a9e1b |  | note | Guidelines: Fire Sprinkler Systems – 1400kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | 9ffe8322-3170-57db-944d-646d9e7cce27 |  | note | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | a709d1ca-2271-5740-beb3-133af25c2c5d |  | note | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
checkpoint-group |  |  | section | Rough In Only OR Rough In & Fit Off Together
checkpoint-status |  |  | checkpoint | First Sighting - Pass once entered
text | a5be484e-7f9e-57f4-91be-a81ca44177de |  | textbox | Date
text | 43a02b71-61e2-5a9e-9cef-8e76f9fe727c |  | textbox | Time
text | d603e98b-8d97-591d-8f79-abebf9d06bb0 |  | textbox | Pressure
button | 9f773511-ce92-5711-a5e4-7c5cd799ac0b |  | button | Photo(s) taken | Yes, No
button | 454ccd64-edca-54cd-9482-589c96d348f2 |  | button | Leemark Sign-Off - Attach below | Pass, Fail
button | 9f5f9a23-4ac4-5e50-aa57-00359a38fd2b |  | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
checkpoint-status |  |  | checkpoint | Second Sighting - Pass once entered
text | 9349e1eb-a068-51ae-9388-1da8366e2453 |  | textbox | Date
text | a106b918-d7c6-55f5-98f4-946f6a084820 |  | textbox | Time
text | 0682ae35-d64e-5288-ae19-11278c090d5b |  | textbox | Pressure
button | 877e5725-8df9-5813-bca9-2ce56f83ab54 |  | button | Photo(s) taken | Yes, No
button | 44545400-1e5a-5c46-9d05-d362cd0e2882 |  | button | Leemark Sign-Off - Attach below | Pass, Fail
button | 01966b48-e281-5c8f-a714-9278e2444917 |  | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
checkpoint-group |  |  | section | Fit Off (if required ie if not covered by the above section)
checkpoint-status |  |  | checkpoint | Subsequent Sighting - Pass once entered
text | 5cb1b3c1-fc98-58ef-b34e-7630d0710a2d |  | textbox | Date
text | d8254998-332d-51bb-ba28-fd51d7f4772e |  | textbox | Time
text | 40126d84-8ab4-525e-b783-c16a86809637 |  | textbox | Pressure
button | 3d259f47-531b-547d-9884-77841eed8990 |  | button | Photo(s) taken | Yes, No
button | 24783c9d-17bf-549c-802d-138feb267135 |  | button | Leemark Sign-Off - Attach below | Pass, Fail
button | 9438b50c-1971-5ce6-9372-76392b6f40bf |  | button | Builder Sign-Off - Attach below | Pass, Fail, N/A
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 46db4572-feb3-5881-b28a-8348c2fa8e14 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | b2cddd83-e0c7-5728-a1d7-ef07676f43cb |  | button | Area left clean & tidy | Yes, No
boolean | ea6aeff1-ce04-5e07-85d9-d7662340291f |  | tickbox | Leemark Sign-Off
boolean | 91c211f4-dab3-5b20-9204-b7fabfbedf37 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) |  |  |  |  | Yes | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) | 56c89b74-4c8d-4506-a47f-63bd1b96fd4a
checkpoint-group |  |  | section | Fit-Off
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 532340ca-c319-5d4d-8102-76ac5db98c61 |  | textbox | Drawing & Revision #
boolean | b88f385c-bfd7-5fd8-9e64-d8a82092389d |  | tickbox | Area clear, tidy and accessible
label | 9646ac9e-39be-5d05-b23f-515ccd4c6623 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all detectors been installed in the correct position and addressed
checkpoint-status |  |  | checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
checkpoint-status |  |  | checkpoint | Have all magnetic door holders been installed correctly
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for security fire trips
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
checkpoint-status |  |  | checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all devices been terminated for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable feeds been connected to the first device
checkpoint-status |  |  | checkpoint | Have all cable feeds been connected to the last device
checkpoint-status |  |  | checkpoint | Have cable feeds been connected at the panel
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Check that all address tags and labels are clear and readable
checkpoint-status |  |  | checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | cd9e24c4-8e86-5c3e-977e-595f418f7597 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 61fda339-1bee-5ec2-a27d-13c4f0a166e8 |  | button | Area left clean & tidy | Yes, No
boolean | 3b0cbb4f-63e7-5e92-98e8-23c10e7dba39 |  | tickbox | Leemark Sign-Off
boolean | a6f30197-0adc-5683-91bb-21e2a27b2f85 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.3 Hose Reel Installation | 616bdab6-4cde-4380-8b21-24fbb5a5069f
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 8a4aa6c4-7b6a-5de5-a752-d448d8b6646a |  | textbox | Drawing & Revision #
boolean | 11534944-4abb-56c1-9a18-4ca779bbe0c9 |  | tickbox | Area clear, tidy and accessible
label | a2e49818-9901-5a9f-a543-6bf09ed3bd97 |  | note | Attach Photos/Comments below if any issues & send report to Builder
text | 3f648ddc-0652-5021-a05f-f38bbab56891 |  | textbox | Hose Reel No.
checkpoint-status |  |  | checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
checkpoint-status |  |  | checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
checkpoint-status |  |  | checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
checkpoint-status |  |  | checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
checkpoint-status |  |  | checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
checkpoint-status |  |  | checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
checkpoint-status |  |  | checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
checkpoint-status |  |  | checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
checkpoint-status |  |  | checkpoint | Any defects found on the hose reel assembly have been corrected
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 2b3fad50-31d0-5eff-a56b-abff2d18959d |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | cb42a527-ef06-59a6-bd5f-282da7750fdb |  | button | Area left clean & tidy | Yes, No
boolean | 37a44799-e5f3-5448-bed4-51b8f1cf320d |  | tickbox | Leemark Sign-Off
boolean | 365082e4-0ac6-5fa5-bd5f-81e71f043abb |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.2 Ewis Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.2 Ewis Installation | 737c53f1-e37e-43e3-a277-f8a294bb3b94
checkpoint-group |  |  | section | Cabling
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | eabd9245-f876-5464-97f6-8263cfbeb9f1 |  | textbox | Drawing & Revision #
boolean | 0bbda881-8616-58be-819a-8b75d3272e18 |  | tickbox | Area clear, tidy and accessible
label | 07a32e0b-1352-5a46-a21a-1eadc1b7fea3 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cables been installed for speakers and horns
checkpoint-status |  |  | checkpoint | Have all cables been installed for warden intercom points
checkpoint-status |  |  | checkpoint | Have all cables been installed for emergency call points
checkpoint-status |  |  | checkpoint | Have all cables been installed for strobes
checkpoint-status |  |  | checkpoint | Have all cables been installed for background music inputs
checkpoint-status |  |  | checkpoint | Have all cables been installed for microphone inputs
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint-status |  |  | checkpoint | Have all cables been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cable feeds been installed in the correct position
checkpoint-status |  |  | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint-status |  |  | checkpoint | Have the modified cable trays been re-galvanized
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 3789ddbe-9093-599e-9443-71d7c53c4699 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 29088802-d955-5436-9514-a5d585e1abda |  | button | Area left clean & tidy | Yes, No
boolean | efaf6c6b-2d2b-5261-9cda-1790db0ce1b1 |  | tickbox | Leemark Sign-Off
boolean | baff02ad-39f8-51c5-b2dc-7a71636ad1a6 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.4 Fire Detection Installation | 7542b106-5571-431d-917c-cd4175b3010b
checkpoint-group |  |  | section | Cabling
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 36bdb376-28a8-59dd-aff5-477f8079547c |  | textbox | Drawing & Revision #
boolean | 0c112bc2-e7ad-5a24-a831-5bbdcceac863 |  | tickbox | Area clear, tidy and accessible
label | f42a78e9-fe83-5bd4-999d-9a0791e0be64 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cables been installed for detectors
checkpoint-status |  |  | checkpoint | Have all cables been installed for sprinkler valve sets
checkpoint-status |  |  | checkpoint | Have all cables been installed for magnetic door holders
checkpoint-status |  |  | checkpoint | Have all cables been installed for security fire trips
checkpoint-status |  |  | checkpoint | Have all cables been installed for mechanical fire trips
checkpoint-status |  |  | checkpoint | Have all cables been installed for AS 1668 Fan Controls
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint-status |  |  | checkpoint | Have all cables been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all cables been joined through for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cable feeds been installed in the correct position
checkpoint-status |  |  | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint-status |  |  | checkpoint | Have the modified cable trays been re-galvanized
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 9b88c54b-9305-52c8-b222-d8babe2bd1f3 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | e967e1a8-f942-5cf3-8ce2-8270fbced84c |  | button | Area left clean & tidy | Yes, No
boolean | a2de1916-7611-58c8-a62f-70df68c9e61e |  | tickbox | Leemark Sign-Off
boolean | f197be1a-87c4-50ba-9d25-0640bc8d5826 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Daysheets (Labour & Materials) |  |  |  |  | Yes | Daysheets (Labour & Materials) (V.180521) | 7d766e6e-2630-498e-8a91-268f6a4fc43e
checkpoint-status |  |  | checkpoint | Daysheet Completed & Ready for Invoicing
text | 931dd1e9-e6f7-5970-96bc-c5fb9280165b |  | textbox | Date
text | 3bff79c6-0816-52cd-9e1f-63cee682347c |  | textbox | Project
text | fadd42ae-e4b2-55ca-840e-a83ee3ddce8b |  | textbox | Location
text | a3f6da3f-5df2-56d2-b92e-0f3d0d2589e6 |  | textbox | Workers Name (Add hours in brackets)
text | 6d361e0f-2263-54e3-b3ca-3bda46ad2f47 |  | textbox | Material 1 (Quantity & Description)
text | e983444b-af8c-5726-bee7-c484318a6209 |  | textbox | Material 2 (Quantity & Description)
text | d7bdc89c-6dca-5cc2-8bf8-22fc1c0e86b9 |  | textbox | Material 3 (Quantity & Description)
text | 509caee7-e268-5f5d-ad4b-0812134a7dcd |  | textbox | Material 4 (Quantity & Description)
text | 6e9d09c8-8a97-5a17-9cdf-0c0915621169 |  | textbox | Material 5 (Quantity & Description)
button | c20aadcd-5e8c-5e28-a24b-24f5efd5259f |  | button | Reviewed by Leemark Supervisor | No,Yes
boolean | 44ff8f03-db9b-5a6b-ace2-12ab20bcdcb2 |  | tickbox | Signature of Builder's Supervisor Added
holdpoint |  |  | signoff | Signature Added - Click Here
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.1 Fire Panel Installation | 7eeff736-d956-43f0-a496-4e634bdf48d9
checkpoint-group |  |  | section | Fire Indicator Panel
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 2bcd482d-ca24-5b6c-ba66-f0b185cf2014 |  | textbox | Drawing & Revision #
boolean | 37743373-936d-5cb0-b95e-3f8a657fdbe6 |  | tickbox | Area clear, tidy and accessible
label | d0e387c7-2bc1-5491-b152-ffb72bd60886 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Are visual indicators and controls not less than 750 mm from the floor
checkpoint-status |  |  | checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
checkpoint-status |  |  | checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
checkpoint-status |  |  | checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
checkpoint-group |  |  | section | Accessibility
checkpoint-status |  |  | checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
checkpoint-status |  |  | checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
checkpoint-status |  |  | checkpoint | Is the door absent of locks
checkpoint-status |  |  | checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
checkpoint-status |  |  | checkpoint | A minimum clearance is maintained from the enclosure as shown
checkpoint-group |  |  | section | Power sources
checkpoint-status |  |  | checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
checkpoint-status |  |  | checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
checkpoint-status |  |  | checkpoint | The battery is not be tapped for intermediate voltages
checkpoint-status |  |  | checkpoint | All connections are made using suitable connectors
checkpoint-group |  |  | section | Sub-Indicator Panels
checkpoint-status |  |  | checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
button | 6cd9ffc9-68db-53e4-9a82-206d7a65d329 |  | button | (a) The SIP serves the entire building | Yes, No, N/A
button | ca9103c4-6046-56b5-b50e-1358ddd84939 |  | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes, No, N/A
button | 0975fc60-601b-5b4a-8896-8291c9e6f69f |  | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes, No, N/A
button | 8b5743b9-ef1d-5e48-a4d2-96044abd2ca5 |  | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes, No, N/A
button | 8e1a4e47-0737-5034-af78-5ca70a206068 |  | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes, No, N/A
checkpoint-group |  |  | section | Wiring
checkpoint-status |  |  | checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
checkpoint-status |  |  | checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
checkpoint-status |  |  | checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
checkpoint-status |  |  | checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 93cd29ae-00fb-5254-a2a7-39b3a4ec9f75 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | a39afb5b-131e-5cba-8341-e96b904b0cc4 |  | button | Area left clean & tidy | Yes, No
boolean | 946a6d04-b6ac-5b20-9638-b171e2260dda |  | tickbox | Leemark Sign-Off
boolean | b1d8dd79-f4b4-5ded-b46f-c4f928185a28 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.4 Tank Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.4 Tank Installation | 889ddaf4-1a06-4078-93a6-63f86860f430
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 0cda1a53-e26d-59af-8c76-52c7f0d309bd |  | textbox | Drawing & Revision #
boolean | 013a852f-427d-54d2-b306-e5c3c0fcfdb5 |  | tickbox | Area clear, tidy and accessible
label | 7ac3b35d-11ee-514d-a735-bda4b9a72cfe |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
checkpoint-status |  |  | checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
checkpoint-status |  |  | checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
checkpoint-status |  |  | checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
checkpoint-status |  |  | checkpoint | Tank drain/sludge isolation valve is fitted and blank off
checkpoint-status |  |  | checkpoint | Tank external water level indicator is fitted and operational
checkpoint-status |  |  | checkpoint | Tank internal and external access ladders are fitted & secured
checkpoint-status |  |  | checkpoint | Tank access hatch is fitted and provided with lockable cover
checkpoint-status |  |  | checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
checkpoint-status |  |  | checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 41f126ba-a256-525c-9a56-fa244444a42f |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 277e41d1-3b5c-5175-ae85-78a993dfda7e |  | button | Area left clean & tidy | Yes, No
boolean | 8a54f009-0ff2-5202-bac9-45d443ab965a |  | tickbox | Leemark Sign-Off
boolean | d791b5d4-0f0d-5ebd-8227-bc1a6529c2be |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50 ITR 303.7 ASD (Aspirated) Installation (V.171121) |  |  |  |  | Yes | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection | 96035eb6-f33c-43a7-850e-aea11c14f2e6
checkpoint-group |  |  | section | Pre-commissioning Procedures
checkpoint-status |  |  | checkpoint | Check the location of installation is as per approved shop drawings and manufactures recommendations
checkpoint-status |  |  | checkpoint | Check the Height of Panel is as per manufacturer's recommendations and in accordance with the relevant Australian Standards
checkpoint-status |  |  | checkpoint | Confirm operation of auto-reset from FIP is wired through GP relay
checkpoint-status |  |  | checkpoint | Check all wiring connections are tight and secure
checkpoint-status |  |  | checkpoint | Check routing of the conduits are as per approved shop Dwg’s
checkpoint-status |  |  | checkpoint | Check joints are properly glued /sealed and bonded to eliminate any potential air leaks
checkpoint-status |  |  | checkpoint | Check pipe joints at the inlet ports of the scanner are not glued but firmly fitted into air inlet socket
checkpoint-status |  |  | checkpoint | Check the sensing holes are drilled as per design
checkpoint-status |  |  | checkpoint | Confirm the exhaust has been routed back into the sampling space
checkpoint-status |  |  | checkpoint | Confirm end caps have been installed un-glued to all pipes at a serviceable height
checkpoint-status |  |  | checkpoint | Confirm wiring is complete to Action, Minor Urgent, Fault & Fire relays and monitored via the FIP.
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Power up the system, the aspirator starts up and air is flowing out of exhaust port , LCD screen is operational.
checkpoint-status |  |  | checkpoint | Induce smoke into the furthest sampling point from the head end unit
checkpoint-status |  |  | checkpoint | Check that a Fire signal is being transmitted to the FIP within 60s of smoke entering the VESDA pipe
checkpoint-status |  |  | checkpoint | Check the correct signals are being transmitted to the FIP via Action, Minor Urgent & Fire Relays correctly.
checkpoint-status |  |  | checkpoint | Remove the power from the VESDA and confirm Fault is received at the FIP
checkpoint-status |  |  | checkpoint | Check the fire signal is conveyed to the fire Alarm system and BMS, if required
checkpoint-status |  |  | checkpoint | Check the transmission of signals to operate ancillary devices, if required.
checkpoint-status |  |  | checkpoint | Record all baseline data as required
checklist-flat |  |  | checklist | Variation |  |  |  |  | Yes | Variation | 96bb78e4-4815-42db-aaa0-23e658fb665a
checkpoint-status |  |  | checkpoint | Variation Details Complete (Pass once inputted)
text | 0cf51977-6d75-5af4-a97d-fbb55832298b |  | textbox | Variation Name
text | 456c7393-3d47-5f94-96fe-dde149bcdf48 |  | textbox | Variation Description
text | 83b89ec8-1776-5044-a934-f4d09f4b1d81 |  | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
text | ec2054e7-1c8c-5337-b42c-32593298a0a6 |  | textbox | Acknowledgement
text | f1d0cdfe-486c-57f8-ab76-60e4a40d8048 |  | textbox | Signature/Reference Mail
checkpoint-status |  |  | checkpoint | Photo(s)
checkpoint-status |  |  | checkpoint | Supporting Documentation (Attached or Referenced)
checkpoint-status |  |  | checkpoint | Variation Sign-Off - Click to Add signatures below
button | 64723357-e840-5990-b650-f9868a197067 |  | button | Leemark Representative Signature Added below | Yes, No
button | 678e2a6c-2c78-56d9-a89f-7bfd9a7761c0 |  | button | Builder Representative Signature Added below | Yes, No
holdpoint |  |  | signoff | Click to Add Signatures
checklist-flat |  |  | checklist | Additional Tasks - add as required |  |  |  |  | Yes | Additional Tasks - add as required | a5c81b1b-284d-4183-81e3-59869095709d
checkpoint-status |  |  | checkpoint | Details of additional tasks - comment below
checklist-flat |  |  | checklist | Additional Tasks Checklist |  |  |  |  | Yes | Additional Tasks Checklist | c7e4bf9b-06b3-4f00-a1b0-ee38a75bf278
checkpoint-status |  |  | checkpoint | Details of additional tasks - comment below
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff |  |  |  |  | Yes | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff | d5759cac-8bbc-4d7e-be10-4b83fd46097c
checkpoint-group |  |  | section | Sprinkler Rough-In
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 0bb47b23-6ddc-5801-a8a8-9c44b250e870 |  | textbox | Drawing & Revision #
boolean | 60f8bb55-fcef-5042-97f9-772377216106 |  | tickbox | Area clear, tidy and accessible
label | c4475655-4fc8-5aa4-897b-0f0fd5c1cf0c |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Supports spacing & fixing as per AS2118
checkpoint-status |  |  | checkpoint | Pipework installed as per drawings
checkpoint-status |  |  | checkpoint | Concealed space sprinklers installed
checkpoint-status |  |  | checkpoint | All ends blanked off/plugged for testing
checkpoint-status |  |  | checkpoint | Pipes left out
label | 3e6c4115-dce8-5b65-9618-ff6da56e1f2a |  | note | Fail=Missing, Pass=Complete
button | 878525ce-d3f1-588e-8cab-2702f7d92dbe |  | button | Pipes left out - installed | Yes, No
checkpoint-group |  |  | section | Sprinkler Fit-Off
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 600928b9-539d-5eeb-ba75-e7c3038cea98 |  | textbox | Drawing & Revision #
boolean | c2f959cd-2cf1-5772-aef3-2f2d3165fb2c |  | tickbox | Area clear, tidy and accessible
label | f68b8caf-345b-57c6-9d9d-4404147023f0 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Ceiling grid levelled
checkpoint-status |  |  | checkpoint | Sprinklers installed as per drawings
checkpoint-status |  |  | checkpoint | Sprinkler Type & temperature as per drawings
checkpoint-status |  |  | checkpoint | All escutcheon plates installed
checkpoint-status |  |  | checkpoint | Areas not fitted-off
label | 517e6754-fa7d-521b-b098-1f9811d71e98 |  | note | Fail=Missing, Pass=Complete
button | e0f9c485-e943-5e96-8f43-da007bec6c96 |  | button | Areas not fitted-off - completed | Yes, No
checkpoint-status |  |  | checkpoint | Client Sign Off Sheets Complete
checkpoint-status |  |  | checkpoint | Painting carried out
checkpoint-status |  |  | checkpoint | Pressure Tested (refer ITR 401) - Completed
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 286e855b-7ca8-572e-af38-fc18dded83f2 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | d3da4035-6e0f-5fee-af39-2ae8f5c1db64 |  | button | Area left clean & tidy | Yes, No
boolean | 4ed9e107-8f9e-5892-8aeb-9bb926369b89 |  | tickbox | Leemark Sign-Off
boolean | 9d237b41-8531-5321-9f7a-d161e8041959 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Document Attachment ITP (V.220421) |  |  |  |  | Yes | Document Attachment ITP (V.220421) | def51b7c-1242-4acd-aa20-59d40d802eb5
checkpoint-status |  |  | checkpoint | Documents/Drawings attached for reference - Pass once attached
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve |  |  |  |  | Yes | LM-FOR-30-ITR-301.2 Alarm Control Valve | f0ac083c-9fb1-4d97-890e-bcb2802b4866
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | f6943492-efa1-54e4-898f-1c6f46035f12 |  | textbox | Drawing & Revision #
boolean | 578fb634-f4e8-59b7-b41d-1cda29c41b05 |  | tickbox | Area clear, tidy and accessible
label | f3d32dab-51c2-5794-abe9-ff636ba421d7 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All supports are completely installed, spaced and bolted down
checkpoint-status |  |  | checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint-status |  |  | checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint-status |  |  | checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
checkpoint-status |  |  | checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
checkpoint-status |  |  | checkpoint | Main waste & test valve is fitted and piped to drain
checkpoint-status |  |  | checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
checkpoint-status |  |  | checkpoint | Correct model and range of Pressure Switch is fitted
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
checkpoint-status |  |  | checkpoint | Control Valve associated pipe works paint touch-up repair is completed
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 2b1f8ab7-84a6-5ff5-bf77-eff2f48fd6a2 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 164d7e91-7c10-527a-854b-3e646f5795f3 |  | button | Area left clean & tidy | Yes, No
boolean | 4094a41c-5dd9-5f55-b241-476550bb6210 |  | tickbox | Leemark Sign-Off
boolean | d33673d8-5ebe-5610-b5c9-53b5e896e0a3 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Site Diary |  |  |  |  | Yes | Add Site Diary Checklist | fa1b38f7-cc84-47e6-85ed-1044aff02e75
checkpoint-status |  |  | checkpoint | Areas of work accessible for the day
select | e048d81c-b120-5201-90b9-737dc818e2c4 |  | dropdown | Day | Friday, Saturday, Sunday, Thursday, Tuesday, Wednesday,Monday
text | 8b06ec40-8a3c-5890-8eef-2138d0007662 |  | textbox | Date
text | 220bbcf8-26f5-50d0-8333-a92a92c45817 |  | textbox | Year
text | 2ee2d4ff-2e7a-5a32-abbd-16864834758c |  | textbox | Number of workers on site
text | f718a78d-8c75-581f-8ecc-f206357c4ca1 |  | textbox | HSR on site today enter name
text | 67e1eae6-6cc5-54f1-9e71-af2e0d4466a4 |  | textbox | First Aider on site today enter name
text | 300a822f-3c8d-5eb4-ace2-997e233cf07a |  | textbox | Injury on site today enter name
checkpoint-status |  |  | checkpoint | Work area 1 details entered
text | 47c51389-20da-5ede-8014-b3d862ef3eaa |  | textbox | Area
select | be2d3209-4753-5610-ab16-ae8739025b3a |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 8e3893b8-ed2f-5026-a09c-93c5cb077f2f |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 2 details entered
text | c3bf60c1-b562-5b80-a516-8f9ebd4704ed |  | textbox | Area
select | 4be3a27e-4b3d-586a-b513-ceb15fc40bfe |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | c2b720eb-8138-59ab-8725-672f980b9236 |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 3 details entered
text | 67ba33fd-a2e8-519a-9718-9602c1c22c34 |  | textbox | Area
select | d67e8a5c-0701-5122-8469-a3f875979c90 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | e0c6f448-ea66-5571-ab37-d4e5b00d7eba |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 4 details entered
text | a65ca3a0-57ef-5fca-9a21-6c58979e77b1 |  | textbox | Area
select | 228c593c-8c7b-556a-a358-a302692731ee |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | be73872c-40d0-5fe1-95e7-28fc71abd66b |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 5 details entered
text | 5c62749c-d156-5f1a-a0db-c1bfbf345bbe |  | textbox | Area
select | fb2b9525-bedc-5e79-8595-7d9e44168dbe |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 0f36562c-85d2-5c15-b10e-0e0351ca42a0 |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 6 details entered
text | df45fc36-050d-52a7-b4de-4c3dfd8b7dc1 |  | textbox | Area
select | ce639f3d-bbb2-5e33-bfa7-831d0f7f3ce4 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 7a39984c-f43a-5db8-bbb8-67cb3b46d3ad |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 7 details entered
text | f56b01be-ce67-517e-9201-21fbb9da80c2 |  | textbox | Area
select | cd1edc93-5190-52b7-8b91-cd4940a807f6 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 0ce609f8-0e23-570c-84bf-8d4ab1c5a902 |  | textbox | Other
checkpoint-no-status |  |  | checkpoint | Work area 8 details entered
text | 87fec433-1b39-5b0c-85ab-47b3724894e7 |  | textbox | Area
select | 497f30d6-7d3e-567a-9fde-26ab4d0ca912 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 64afa6dd-5e29-541b-8f7a-b3eefebb69ef |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Weather conditions entered
select | e4a9dd83-8a46-5d40-9016-ecdf1143b19f |  | dropdown | Conditions: | Hot, Overcast, Rain, Showers, Windy,Fine
text | c4eca12e-6581-575e-a282-008a28f85230 |  | textbox | Min temp predicted
text | 9f6d3c08-4655-5cb2-a2ec-d500dc6aaf2c |  | textbox | Max temp predicted
checkpoint-no-status |  |  | checkpoint | Delays from inclemency
text | f4baf749-c7b9-5264-82f9-225bad01bac5 |  | textbox | Total Hours of delay
select | c7cb66ed-53d5-5a5a-8876-a70cef304006 |  | dropdown | Conditions: | , Heat, Other trades, Windy,Rain
checkpoint-no-status |  |  | checkpoint | Delays from Builders or Others
text | afcd53cc-c4ba-599f-8ce0-c3160cb74e57 |  | textbox | Total Hours of delay
select | c19fccf4-46f7-5cda-af3d-ffd8ba800343 |  | dropdown | Conditions: | Concreter, Crane, Earthworks, Other, PT, Safety, Scaffold, Steel fixer, Union,Builder
checkpoint-status |  |  | checkpoint | Attach Specific site photos for respective day
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.5 Booster Assembly |  |  |  |  | Yes | LM-FOR-40-ITR-302.5 Booster Assembly | fb37e1d3-8576-4031-8f79-dc282f42f98a
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 59e5dd48-bdeb-58b2-951b-77ff909c8789 |  | textbox | Drawing & Revision #
boolean | 8507565f-78eb-55eb-b4a8-fb4a687d0bf7 |  | tickbox | Area clear, tidy and accessible
label | 81689dec-7ac0-548f-be1a-423f6ab696ac |  | note | Attach Photos/Comments below if any issues & send report to Builder
checkpoint-status |  |  | checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
checkpoint-status |  |  | checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
checkpoint-status |  |  | checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
checkpoint-status |  |  | checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
checkpoint-status |  |  | checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
checkpoint-status |  |  | checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
checkpoint-status |  |  | checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
checkpoint-status |  |  | checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
checkpoint-status |  |  | checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
checkpoint-status |  |  | checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
checkpoint-status |  |  | checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
checkpoint-status |  |  | checkpoint | Full flow non-return valve of correct size is installed in the proper location
checkpoint-status |  |  | checkpoint | Approved type of cabinet enclosure is installed as required
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | 5c5ef7fd-1c12-599d-b418-3b426c96565c |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 7f400896-2761-5efa-a61d-13abca64fb49 |  | button | Area left clean & tidy | Yes, No
boolean | 8acb0637-7da4-564a-96c5-ce92bf5530da |  | tickbox | Leemark Sign-Off
boolean | 2c5c554a-07e4-5dc7-94d5-8d9021829971 |  | tickbox | Builder Sign-Off
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)