## Sheet1
type | name
checklist | Auxiliary Panel
section | Information
checkpoint-no-status | Auxiliary Panel Check Sheet
textbox | HV Cable number
textbox | Area
textbox | Drawing reference
textbox | Panel name
section | Pre-Installation
checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. (Hold Point)
checkpoint | 1.02 Verify drawings latest revision. (Hold Point)
checkpoint | 1.03 Confirm delivery & unloading plan for the switchgear is approved. (Hold Point)
checkpoint | 1.04 Make sure traffic management plan is approved if required during transportation. (Hold Point)
section | Installation
checkpoint | 2.01 Ensure that the switchgear make/model is as per the design drawings.
checkpoint | 2.02 Ensure that enclosure is relocated by the lifting hooks / points provided, the asset has been protected and no damage has been caused during movement. (Monitor)
checkpoint | 2.03 Ensure to provide lifting equipment at the site and obtain traffic management plans if required.
checkpoint | 2.04 Off-load the equipment and carefully move it into final position. (Monitor)
checkpoint | 2.05 Install the switchgear over the appropriate wall space. Ensure to install the switchgear as per manufacturer's instructions.
checkpoint | 2.06 Bolt down the switchgear assembly base frame with M12 bolts. Shim and grout if necessary to ensure level adjustment and alignment with adjacent panels.
section | Switchgear Interconnection
checkpoint | 3.01 Verfiy all switchgear interconnections have been made by the manufacturer and no on-site connections are required.
section | Confirmation of installation & Documentation
checkpoint | 4.01 Confirm all accessories have been factory fitted.
checkpoint | 4.02 Do Inspection after installation for complete switchgear assembly.
checkpoint | 4.03 Verify type main isolator rating. (Monitor)
checkpoint | 4.04 Panel is ready for termination of Power cables & control cables. (Hold Point)
checkpoint | 4.05 Mark up "As built" drawings.
section | Signoff
signoff | Supervisor
signoff | Project Engineer
signoff | Client