## Sheet1
type | name
checklist | HV Cable Installation
section | Information
checkpoint-no-status | HV Cable Installation Check Sheet
label | Project: P.0597875 - AIAL WP1
textbox | Area
textbox | Drawing reference
textbox | HV Cable number
section | Planning
checkpoint | 1.01 Verify drawings latest revision. (Hold Point)
checkpoint | 1.02 Cable route/installation methodology: - Verify that cable Install design route suits site conditions. - Ensure the cable route has been assessed. (Cable hauling analysis) - Pulling, jointing, & termination pits have been correctly formed and positioned. (Hold Point)
checkpoint | 1.03 All required documents & permits have been approved and issued (PTW, TMP, SWMS, and methodology). (Hold Point)
checkpoint | 1.04 All staff and subcontractor have been fully site inducted and briefed on HSE & install methodology. (Hold Point)
checkpoint | 1.05 Ensure that the pre-installation tests on the cable has been completed, reviewed, and accepted. (Hold Point)
section | Pre-Installation
checkpoint | 2.01 Verify that cable pulling equipment are of adequate capacity to provide a steady continuous pull on the cable. (Hold Point)
checkpoint | 2.02 All site modified sections of cable management have been correctly cut; filed and treated as required.
checkpoint | 2.03 All conduit interiors should be free of burrs and have been cleaned after installation.
checkpoint | 2.04 Sharp Edges of cable management have been rounded. All cut ends are neat, square and treated as required.
checkpoint | 2.05 Ensure that cable duct has an appropriately rated draw wire or equivalent installed through the entirety of cable route.
checkpoint | 2.06 Verify that all cable ducts are free from water and debris. If open trench - ensure that trenches have a bedding layer in the base of the trench to the correct depth. (Hold Point)
checkpoint | 2.07 An appropriately-sized mandrel should be pulled through all underground ducts prior to cable pulling. Any abrasions or sharp edges that might damage the cable should be removed.
checkpoint | 2.08 An appropriately-sized foam pig/squeegee should be pulled through all underground ducts prior to cable pulling.
checkpoint | 2.09 Verify that a suitable feeder device is used to protect and guide the cable from the cable reel into the raceway. The radius of the feeder device should not be less than the minimum bending radius of the cable. If a feeder device is not used, the cable should be hand-guided into the raceway.
checkpoint | 2.1 Ensure sufficient labour is available, and correctly positioned along the cable route. (Monitor)
checkpoint | 2.11 Ensure adequate communication method/supervision is available and agreed for the cable pull (two-way radio, line of sight, etc.) (Hold Point)
section | Installation
checkpoint | 3.02 Any cable pushing devices should be monitored to synchronise with the tension of the cable winch to avoid kinking the cable. (Monitor)
checkpoint | 3.03 Pulling tension will be increased when the cable is pulled off the reel. Turn the reel and feed slack cable to the duct entrance to reduce the pulling tension. (If applicable) (Monitor)
checkpoint | 3.04 Log continuous readings of the dynamometer incorporated in the pulling arrangement to enable the actual pulling tension to be monitored. Pulling tension shall not exceed manufacturer's requirements. (If applicable) (Monitor)
checkpoint | 3.05 Ensure cable manufacturer’s minimum allowable bending radius and sidewall pressures for cable installations are not violated. (Monitor)
checkpoint | 3.06 Cables identified by a permanent marker at each end in accordance with the design documents.
section | Confirmation of install
checkpoint | 4.01 Vertically run cables are supported by holding devices in the tray, in the ends of the conduit, or in boxes inserted at intervals in the conduit system. (If applicable)
checkpoint | 4.02 Cables installed in vertical cable tray are secured as per manufacturer's recommendation.
checkpoint | 4.03 Cables installed in trays are neatly arranged to facilitate identification and removal and to maximize tray fill. (If applicable)
checkpoint | 4.04 Cables installed in trenches have a minimum separation distance as prescribed in the design drawing and not less than 150 mm
checkpoint | 4.05 Cables installed in trenches have polymeric cable protection complying with AS/NZS 4702 covers as prescribed in the design drawings.
checkpoint | 4.06 Cables installed in reduced depth trenches have a capping of unreinforced concrete as prescribed in the design drawings. (If applicable)
checkpoint | 4.07 Cables installed in trenches have underground marking tape complying with AS/NZS 2648.1 as prescribed in the design drawings.
checkpoint | 4.08 Cable duct ends have been sealed with expanding foam or cable duct sealant. (where applicable)
checkpoint | 4.09 The exposed ends of all cables installed but not terminated shall be covered with a protective end cap.
checkpoint | 4.10 Lengths of cable cut from a drum or when the drum is not emptied completely, the ends of any cut length are sealed with an end cap, such as a heat shrink end cap, to prevent the ingress of moisture.
checkpoint | 4.11 As built information completed and submitted for review. (Hold Point)
section | Signoff
signoff | Supervisor
signoff | Project Engineer
signoff | Client