## Sheet1
type | name
checklist | HV Cable Termination
section | Information
checkpoint-no-status | HV Cable Termination Check Sheet
label | Project: P.0597875 - AIAL WP1
textbox | Area
textbox | Drawing reference
textbox | HV Cable number
section | Pre-Installation
checkpoint | 1.01 All staff briefed on safety requirements and installation procedure.
checkpoint | 1.02 Inspect that cables do not make contact with sharp-edged sheets in the switchgear. Cover sharp-edged spots, if required.
checkpoint | 1.03 Verify drawings latest revision.
checkpoint | 1.04 Ensure the equipment is secured firmly to the earthing.
checkpoint | 1.05 Equipment frame connected to main earth bar.
checkpoint | 1.06 Cable box bushing earthed by switching associated earthing switch to ON.
checkpoint | 1.07 Confirm correct cable termination kits supplied. Ensure voltage level, bushing type, indoor/outdoor, correct diameter.
checkpoint | 1.08 Cable box and switchgear terminations are suitable for the cable size.
checkpoint | 1.09 Verify that visible cable bends meet or exceed manufacturer's minimum published bending radius. (Witness)
checkpoint | 1.10 Inspect bolted electrical connections for high resistance using one or more of the following: - Use a low-resistance ohmmeter - Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method in accordance with manufacturer's published data. (Hold Point)
checkpoint | 1.11 Ensure Cable Terminations ITP's Template received and verified. (Witness)
section | Installation
checkpoint | 2.01 Correct bend radii observed. Record cable bending radius.( Witness)
checkpoint | 2.02 3-core breakout sheath installed at end of cable over sheath.
checkpoint | 2.03 For breakout outside termination chamber, verify gland plate is non-ferrous.
checkpoint | 2.04 Prepare cable gland plate, measured to the cable diameter (if not pre-cut).
checkpoint | 2.05 Ensure HV cables are supported/clamped as necessary.
checkpoint | 2.06 Ensure no weight/pressure on terminals/bushings.
checkpoint | 2.07 Must be clamped prior to connected cable to bushing, to avoid damage to bushing.
checkpoint | 2.08 Ensure correct phase rotation is followed. Cable core identified by a label or marked. (Monitor)
checkpoint | 2.09 Adjust the cut lengths of each cable to each phase, do not use a bar to pull and fit lugs.(Monitor)
checkpoint | 2.10 Unwind, braid and terminate the cable screen connect the cable to a suitably sized cable lug.
checkpoint | 2.11 Check all cable screens double-point bonded (connected at both ends). (Hold Point)
checkpoint | 2.12 Prepare the cable termination in accordance with the instructions provided with the manufacturer's termination kit. (Monitor)
checkpoint | 2.13 Cable connections torqued to correct setting .
checkpoint | 2.14 Cable cores identified.
checkpoint | 2.15 Cable box connection screws are fastened according to specified torque. (M8 at 20Nm & M6 @ 8.5Nm).
checkpoint | 2.16 Photographic evidence taken and recorded. (Hold Point)
section | Confirmation of the installation
checkpoint | 3.01 Cable termination completed and signed ITP received. (Hold Point)
checkpoint | 3.02 Correct bend radii observed. Record cable bending radius. (Hold Point)
checkpoint | 3.03 Cable cores identified. (Hold Point)
checkpoint | 3.04 Termination chamber closed, sealed and no tools or detritus left inside. (Hold Point)
section | Signoff
signoff | Supervisor
signoff | Project Engineer
signoff | Client