## Sheet1
type | name
checklist | Ripple plant installation
section | Information
checkpoint-no-status | Ripple plant installation Check Sheet
label | Project: P.0597875 - AIAL WP1
textbox | Area
textbox | Drawing reference
section | Pre-Installation
checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. (Hold Point)
checkpoint | 1.02 Verify drawings latest revision & all factory documents provided. (Hold Point)
checkpoint | 1.03 Confirm delivery & unloading plan for the switchgear is approved. (Hold Point)
checkpoint | 1.04 Make sure traffic management plan is approved if required during transportation. (Hold Point)
section | Installation
checkpoint | 2.01 Ensure ripple plant make/model is as per the design.
checkpoint | 2.02 Ensure that R800 panel enclosure is relocated by the lifting hooks / points provided, the asset has been protected and no damage has been caused during movement.
checkpoint | 2.03 Ensure to provide lifting equipment at the site and obtain traffic management plans if required.
checkpoint | 2.04 Off-load the equipment and carefully move it into final position.
checkpoint | 2.05 Install the panel over the appropriate wall space. Ensure to install the panel as per manufacturer's instructions.
checkpoint | 2.06 Bolt down the base with M12 bolts. Shim and grout if necessary to ensure level adjustment and alignment with adjacent panels.
checkpoint | 2.07 Ensure there is no mechanical stress on isolators of the coupling capacitors and isolating transformers. (Do not push, pull or lift the isolators.
checkpoint | 2.08 The capacitor is designed for upright installation only. Other mounting positions must be discussed and agreed upon when placing the order.
checkpoint | 2.09 To ensure proper cooling the distance between coupling capacitor units and if necessary to lateral walls should not be less than 70mm.
checkpoint | 2.1 The coupling capacitors should be installed in such a way that the name plate remains visible. Inputs and outputs are interchangeable.
checkpoint | 2.11 Connections to the capacitor terminals should be flexible.
checkpoint | 2.12 The mounting of the tuning coils is options: veritical, horizontal or hanging. Double tuning coils must be installed vertically.
checkpoint | 2.13 Ensure the distance between tuning coilds have to be as big as possible. It must be possible to access the taps at all times.
checkpoint | 2.14 The axis of the center tuning coil must be turned 90deg compared to the two exterior coils.
checkpoint | 2.15 The coils are marked with the direction of the magnetic field, the arrows of both the exterior coils must point in the same direction.
checkpoint | 2.16 The isolating transformer must not be subjected to mechanical stress. Flexible connections are not essential.
section | Switchgear Interconnections
checkpoint | 3.01 Connections to the capacitor terminals should be flexible. This can be achieved through suitable conductor routing or even better through flexible connecting elements.
checkpoint | 3.02 The outgoing connections of tuning coils are connected to the centre bolt. The connection nuts should be adjusted to the greatest possible distance from the movable strap to allow the setting to be readjusted with ease.
checkpoint | 3.03 After mounting, the accompanying warning signs are to be fixed at a well visible place.
checkpoint | 3.04 The isolating transformer low voltage side should be connected in such a way that the changeover to another connection can take place without difficulty. The neutral point of the low voltage side must not be connected.
checkpoint | 3.05 Before putting into operation check the oil level with the oil level gauge and remove the transport gasket from the ventilator cap.
section | Confirmation of the installation
checkpoint | 4.01 Ensure the all components of Ripple plant are earthed to the earth studs. (Hold Point)
checkpoint | 4.02 Manufacturers rep sign off on completion of installation. (Hold Point)
checkpoint | 4.03 Ensure Landis+Gyr Test results and AS-Built drawings are received and verified. (Hold Point)
section | Signoff
signoff | Supervisor
signoff | Project Engineer
signoff | Client