## Sheet1
type | name
checklist | PC69 Switchgear Installation
section | Information
checkpoint-no-status | PC69 Switchgear Installation Check Sheet
label | Project: P.0597875 - AIAL WP1
textbox | Area
textbox | Drawing reference
textbox | Switchboard name
section | Pre-Installation
checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. (Hold Point)
checkpoint | 1.02 Verify drawings latest revision & all factory documents provided. (Hold Point)
checkpoint | 1.03 Confirm delivery & unloading plan for the switchgear is approved. (Hold Point)
checkpoint | 1.04 Make sure traffic management plan is approved if required during transportation. (Hold Point)
section | Installation
checkpoint | 2.01 Ensure the 11kV switchgear is Schneider manufacture.
checkpoint | 2.02 Uplift the switchgear and its ancillary items from the storage facility.
checkpoint | 2.03 Ensure to provide lifting equipment at the site and obtain traffic management plans if required.
checkpoint | 2.04 Deliver the equipment as separate panels. Off-load the equipment and carefully move it into the switchroom.
checkpoint | 2.05 Ensure switchroom floor is as per switchgear installation manual and drawing requirement.
checkpoint | 2.06 Install the switchgear over the appropriate floor opening, as shown in the substation layout drawings. Ensure to install the switchgear as per manufacturer's instructions.
checkpoint | 2.07 Ensure the installed rails/plinth are entirely suitable (levels, positions, etc) for mounting the switchgear.
checkpoint | 2.08 Confirm fixings are suitable and all seismic requirements met.
checkpoint | 2.09 Bolt down the panels as per manufacturer's instructions and under the supervision of a Schneider representative. Ensure the panels are accurately positioned due to minimal tolerances of ±1mm per meter and ±2mm for the entire length of the switchboard.
section | Switchgear Interconnections
checkpoint | 3.01 Make sure all necessary secondary connections are made in line with the relevant schematic diagrams.
checkpoint | 3.02 Ensure to supply and install all the AC, DC, CT, VT, intertripping, SCADA and comms cabling to the switchgear panels as per the design drawings and cable schedules provided.
checkpoint | 3.03 Make sure all free-issued communication cables between relays are installed.
section | Confirmation of the installation
checkpoint | 4.01 Manufacturers rep sign off on completion of installation. (Hold Point)
checkpoint | 4.02 Ensure Schneider Test results and AS-Manufactured drawings are received and verified. (Hold Point)
section | Signoff
signoff | Supervisor
signoff | Project Engineer
signoff | Client