## Sheet1
type | name
checklist | Transformer Installation
section | Information
checkpoint-no-status | Transformer Installation Check Sheet
label | Project: P.0597875 - AIAL WP1
textbox | HV Cable number
textbox | Area
textbox | Drawing reference
textbox | Tranformer name
section | Pre-Installation
checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. Ensure position and orientation of the Transformer is understood and agreed.
checkpoint | 1.02 Transformer site agreed by the client. Ensure the base/foundation has attained required MPA strength. (Hold Point)
checkpoint | 1.03 Verify drawings latest revision.
checkpoint | 1.04 Confirm nameplate data matches drawings/design. (Hold Point)
checkpoint | 1.05 Transformer Factory Acceptance Test (FAT) documents received from supplier.
checkpoint | 1.06 Confirm delivery & unloading plan for the transformer is approved. (Hold Point)
checkpoint | 1.07 Make sure traffic management plan is approved if required during transportation. (Hold Point)
checkpoint | 1.08 Inspect transformer and confirm no corrosion or damage to core, base or enclosure. (Hold Point)
checkpoint | 1.09 Confirm oil level are adequate. (Hold Point)
checkpoint | 1.1 Baseline oil sample taken for Dissolved Gas Analysis (DGA) (if required by client).
checkpoint | 1.11 Verify the bushings are clean. (Witness)
checkpoint | 1.12 Confirm the transformer compound has been constructed to requirements and concrete structure is adequately cured and ready for load. (Hold Point)
checkpoint | 1.13 Verify the HV and LV orientations. (Witness)
checkpoint | 1.14 Lift plan produced and reviewed by OMX and client where applicable. (Hold Point)
section | Installation
checkpoint | 2.01 Attach lifting hooks to the crate and perform all lifts using minimum two slings and lifting device, maintaining equal distance between the lifting hooks. (Monitor)
checkpoint | 2.02 Off-load the equipment and carefully position into the compound. Verify the orientation of the HV and LV. Ensuring the alignment of any rigid cable duct (if applicable). (Monitor)
checkpoint | 2.03 Secure the transformer assembly base frame to the allocated site. Shim and grout if necessary to ensure level adjustment.
checkpoint | 2.04 Confirm fixings are suitable and all seismic requirements met. (Monitor)
checkpoint | 2.05 Ensure clean terminal surface, winding casing and enclosure.
checkpoint | 2.06 Ensure all bolts tightened as specified including: holding down bolts, enclosure fixings, earth bonding connections, gland plates.
checkpoint | 2.07 Photographic evidence taken and recorded.
section | Post Installation
checkpoint | 3.01 Inspect anchorage, alignment, and earthing.
checkpoint | 3.02 Inspect bolted electrical connections for high resistance using one or more of the following: - Use a low-resistance ohmmeter - Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method in accordance with manufacturer's published data. (Hold Point)
section | Signoff
signoff | Supervisor
signoff | Project Engineer
signoff | Client