## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Ducting Inspection Record |  | Ducting Inspection Record | 39301e7c-93c6-4d8c-bf9a-77e4e816b6a3
| section | Details
| checkpoint | Details:
88730f1b-4d27-55a0-bdeb-99273c0332b8 | textbox | Contract Name:
d47a87c9-8824-57a9-bbd9-7ee0e879bf6c | textbox | Contract No:
a17477ee-612f-5db6-9195-2cc8b71de68f | textbox | Location:
8aa2ba91-90e9-518d-bd54-c770fce6629c | textbox | Other:
1bd3ceeb-0a0c-5a66-8664-a6cdb1d53526 | textbox | Drawings & Revision No.:
45e822f6-34e6-5a64-85a8-05652162bb5c | date | Date:
2eef4b6f-e28b-5450-86dd-9e3260d2c457 | textbox | Duct Descriptions:
| section | Preliminary
| checkpoint | IFC Drawings Available
| checkpoint | Setout Completed
| section | Excavation/Trenching
| checkpoint | Excavation/Trench to Correct Line and Level
| checkpoint | Subgrade in Trench Tested and Passed
| section | Ducting Inspection Record
| checkpoint | Ducts Installed as Per IFC Drawings
| checkpoint | Any Additional Ducts not on IFC Drawing
| checkpoint | Minimum Duct Separation Maintained
| checkpoint | Joints Cleaned and Glued Correctly
| checkpoint | Ducts Installed to Correct Line and Level
| checkpoint | Installed Ducts Recorded by GPS
| section | Backfill
| checkpoint | Thermal Bedding Under Ducts as Required
| checkpoint | Thermal Bedding Backfilled to Correct Level
| checkpoint | Compaction of Thermal Bedding as Per Agreed Methodology and Passed
| checkpoint | Marking Tape Installed Over Ducts Correctly
| checkpoint | End of Ducts Capped/Taped
| checkpoint-no-value | Comments:
| checkpoint | Ducts and Backfill Checked and Accepted
cb4ddbed-fc6d-56cf-89c7-6941d5e1e9bf | textbox | Name:
b97a8e86-1c13-55f6-9388-1228af8237d4 | date | Date:
| signoff | Sign:
| checklist | ITP 01 - PCS Foundations |  | PCS Foundations | dc37db2b-ed8d-4af2-ad41-deab064829df
| section | Pre Construction
| checkpoint | Review of proposed work
a015857a-71d5-5832-af51-7d6ef368be0c | note | SPECIFICATION REFERENCE - 1235 SHOP DRAWINGS - ITEM 1.10
ef6c6de1-ee59-5ee5-a429-24e7eaf63309 | note | TEST REQUIRED - Shop drawings to be reviewed and permission to proceed given.
154e7045-facf-5dff-bbd6-adaf0b7b27c7 | note | INSPECTION BY - Named reviewer or contract administrator
b80015e9-965f-5c56-97ba-c9f5bbfbe1af | note | TASK TIMING OR TASK FREQUENCY - Start of task
01b7eda7-c416-5a85-9668-3f87820e9018 | note | ACCEPTANCE CRITERIA - Shop drawings to be accepted by the reviewer. Building Information Model (BIM) is being used for the construction works.
a14759cf-37fa-5c62-a4ee-085b9c2d8059 | note | UCCL - H
102e5c1a-6d9f-5324-9fbd-1e30888e6301 | note | Client - A
| signoff | HOLD POINT
| section | Materials
| checkpoint | Concrete Mix Design
1ff17b05-ad05-519b-8bb0-633ac33753bc | note | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
a97a66fb-6048-505d-9577-044ae72fa206 | note | TEST REQUIRED - Supplier Documentation
19053180-29e3-5142-bb96-ec69b2746d52 | note | INSPECTION BY - UCCL, MEL
6e1d0e1e-e0a6-548b-8a20-77e919d36dbb | note | TASK TIMING OR TASK FREQUENCY - Each Mix Design used prior to use
7cf45f41-f19b-567b-adf7-c19477e09adc | note | ACCEPTANCE CRITERIA -
784760dc-6471-5854-9bb7-169773a952c7 | note | Foundations (including retaining wall footing) -
f41ee08c-ccd7-537d-835f-dbf98dd3b45e | note | ○ Aggregate: 19mm
a96be871-a299-5bba-b467-7a3fa0f91799 | note | ○ 28 day strength: 35MPa
218d7da3-68d8-552d-b337-0ef392350e92 | note | Precast retaining wall -
81f3773d-63ee-5d7a-86d0-a28f1edd7909 | note | ○ Aggregate size: 19mm
d84c6630-bdb4-552f-b2f0-82858c4c4f0f | note | ○ 28 day strength: 35MPa
b1bbf60d-f1fa-5abe-85df-986361ab9375 | note | UCCL - S
742f6370-e41b-5bc0-b3a7-04d65bff03cb | note | Client - R
| checkpoint | Certificates
7b0ebe92-d0e8-56d9-96e0-7714567f4052 | note | SPECIFICATION REFERENCE - 1.12 Certificates
acbe2368-d88f-53b7-8c03-c375576d52bb | note | TEST REQUIRED - Portland cement to NZS3121,
f838c7b4-d67c-53d3-912e-e1aef33f670e | note | INSPECTION BY - UCCL
5c21c7de-3680-5303-80a5-55fa6b07158a | note | TASK TIMING OR TASK FREQUENCY - Each Batch
165ace66-0be6-5fa8-ace6-90b106e520c6 | note | ACCEPTANCE CRITERIA - NZS 3122
5ee59556-dd41-57ea-81c9-d5eb6b6e3890 | note | UCCL - S
2b3f94ef-9938-5352-899d-da864a02cb24 | note | Client - R
| checkpoint | Reinforcement
c3148d81-749a-514d-b3fd-f91ef51bb6f9 | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
4dbe8d17-c8d0-519c-95f9-628dae26e814 | note | TEST REQUIRED - Supplier Documentation, photos of spacings
3ae3e378-ab26-5b93-8fcc-9f130e8a96e0 | note | INSPECTION BY - UCCL, MEL
f7d3a9c9-b6fd-57bb-8811-82a222db6718 | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
bfa44109-6c4b-588b-9946-3bf5018d47c5 | note | ACCEPTANCE CRITERIA - Reinforcement of precast retaining wall to be YD12-200 vertical and horizontal with D12-200 starters. Reinforcement of in-situ strip footing to be 2/YD12 with R6-300 stirrups
761c31ac-d8be-5118-a49b-466366c5a7d0 | note | UCCL - V
546aed7c-8fae-578d-bef2-b75478898024 | note | Client - R
| checkpoint | Strip Footing
60946fb8-9c9a-5fe2-84ed-d69c874b85f1 | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
4d5da26e-cae4-5f25-ad5a-a35df12e4627 | note | TEST REQUIRED - Photos
692164fc-48cb-5fd5-a003-c35658400a2a | note | INSPECTION BY - UCCL, MEL
e98962aa-a219-51df-a1a9-29c4ba1af75d | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
4a636711-f2a7-5553-b860-961af734b14b | note | ACCEPTANCE CRITERIA - Reinforcement to have maximum 75mm clearance and minimum 50mm clearance.
| checkpoint | Cast in Items - Nuts, Bolts and Studs
28090b9a-138a-5fc3-acb1-d6daf3d28896 | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-10
2c5cfa97-9d67-5203-99ec-6ba421522912 | note | TEST REQUIRED - Supplier Documentation
55e1de77-fe1a-561a-886c-fc48c5a88179 | note | INSPECTION BY - UCCL
05f3ed75-f9ba-5f52-bdef-cece9de0734a | note | TASK TIMING OR TASK FREQUENCY - Prior to Ordering
58eb0dab-8ad9-54ac-8e28-96ff93fe5390 | note | ACCEPTANCE CRITERIA - EA bolts to be M16 Hilti RE-500
d0abf167-119c-5412-ab02-cda277d6b166 | note | UCCL - V
c9e7c594-bc0a-5d0c-b107-83e30f8d1613 | note | Client - R
| checkpoint | Air content test
e71e4264-4ee2-59ee-9e65-703476b4ee69 | note | SPECIFICATION REFERENCE - 1.13
265ca5d3-6375-5dd6-aee1-302c2bf0456a | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
b1c29214-691d-5f5b-bdc4-4438afc6cafa | note | INSPECTION BY - UCCL
49e6fff7-e796-5652-9518-2256feed20e6 | note | TASK TIMING OR TASK FREQUENCY - Each Batch
acb68691-b603-5081-9d26-de7e519de028 | note | ACCEPTANCE CRITERIA - NZS3109
a73214a9-af49-552b-af6a-9a0be30cd862 | note | UCCL - V
de677fbb-78ef-502f-9833-600a89ea6d48 | note | Client - R
| checkpoint | Slump Test
cd3ad7ef-006d-54bf-bd65-44906a2c20dd | note | SPECIFICATION REFERENCE - 1,13
3982c0cf-80d2-58b7-b2ee-83b2a089daac | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
e148d26b-6899-5609-ab80-e89f551ebee1 | note | INSPECTION BY - UCCL
f32983b1-aaf3-55d0-a5ae-0a705e7d993e | note | TASK TIMING OR TASK FREQUENCY - Each Batch
80471948-7ff8-57fa-8ee6-aed5e29b82b8 | note | ACCEPTANCE CRITERIA - NZS3109
443e0c3e-59df-5c2d-bcf6-0e772d536854 | note | UCCL - V
1f69e207-fa85-5f4e-8e6f-be93e62ea5a5 | note | Client - R
| checkpoint | Conduct 7 day strength test
8fe6f766-0692-5a23-a8ea-b0e94b7b5bca | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.11
a98406e3-7bcc-59cd-a45d-baec1b973dc1 | note | TEST REQUIRED - 7 day strength test
7c48a5af-d2f5-5498-b7f5-ae3772e2d5c4 | note | INSPECTION BY - UCCL
c2462735-2ebc-5691-ae75-97f9f7f74cb3 | note | TASK TIMING OR TASK FREQUENCY - 7 day after casting
4896c328-d859-56ac-beda-7da38e6bb1c8 | note | ACCEPTANCE CRITERIA - 60 % of the specified strength
af51b19a-a39d-5c0a-9c50-a06f6a6abb76 | note | UCCL - V
27a86699-6395-507f-bc02-2135478b07f7 | note | Client - SU
| section | Pre Construction - Site works
| checkpoint | Strip Footing
97fd9e45-7600-5239-98d8-5e0b6ea92c04 | note | TEST REQUIRED - Photos
ee5e2a21-cbc9-54b9-bf45-b0a043b487b2 | note | INSPECTION BY - UCCL
624d746a-0910-5325-9fc7-1f8ed8c4239a | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
fd4ac82a-f2b7-530e-b3b5-b74e445a5e24 | note | ACCEPTANCE CRITERIA - Strip footing to be 400mm wide and 200mm deep
6ff6d2d6-995e-597f-a405-270160a74f7e | note | UCCL - V
edca2f0f-5dd5-509f-ab79-b566aa189426 | note | Client - Su
| checkpoint | Subgrade Strength
832ef7cb-d385-536c-a083-7de4b2426be7 | note | TEST REQUIRED - Scala Penetrometer Records
c3547d4a-b953-54ec-bd05-67653c21325d | note | INSPECTION BY - UCCL
84bcf3ae-d67f-5c4c-b558-76e01f290e59 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
4fb1def6-7272-586a-9a8e-4b8c06fbf852 | note | ACCEPTANCE CRITERIA - Subgrade to meet 3 blows/ 100mm with scala testing
897f8fd4-14d8-5a85-bfec-4dd7082debb5 | note | UCCL - V
27610774-8d12-54dc-9b76-e2c5ee633443 | note | Client - W
| checkpoint | Formwork
33d9f5e3-95a1-5db3-a693-dec849aeb1f3 | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
2de8e55a-cc7e-5d3e-927c-abfca5f48583 | note | TEST REQUIRED - Quality shape and size of formwork
5d661063-20e9-5f63-9017-f9108587ffab | note | INSPECTION BY - UCCL
4bef5f18-7c3e-5f4d-9f5a-416954a6f7b5 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
f9fd92d0-d97c-5f61-b5be-8a69c989f294 | note | ACCEPTANCE CRITERIA - All formwork to meet the specification required for the unit being constructed
206a427d-85f9-5261-b621-72b5a8fe4abd | note | UCCL - V
e106806e-b7f2-5384-b2e6-75bec8e00baa | note | Client - W
| checkpoint | Site Concrete
4ccaa8d5-1b08-5404-9fed-fd9c7499fe90 | note | TEST REQUIRED - Visual inspection
c09a95a8-e2aa-55e9-9123-44aefdc3b3c1 | note | INSPECTION BY - UCCL
94e43f08-d88c-5c9b-ac72-666deb9d9d93 | note | TASK TIMING OR TASK FREQUENCY - Each Foundation
66852368-6cf6-5f78-ba39-90b0b5d15e10 | note | ACCEPTANCE CRITERIA - Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm
e58d6350-7e61-53cc-a1e1-26824ede22dd | note | UCCL - V
9ec2bcef-e924-5179-af65-778129058ea4 | note | Client - Su
| checkpoint | Setout
5e3d1f35-246f-5fc3-ac99-738eb9881095 | note | TEST REQUIRED - Survey
9fedaf09-cf79-5507-a19d-93f597687ed1 | note | INSPECTION BY - UCCL
32b144b7-7e58-5dbe-ab69-7fce691032cd | note | TASK TIMING OR TASK FREQUENCY - Each string
59db3571-2a56-5a11-b072-6c0d16bf7a86 | note | ACCEPTANCE CRITERIA - Foundations and embedded items shall be set out following the tolerances, heights and positions shown in each foundations respective drawing.
8a63898a-42c2-5474-8721-1562ee265996 | note | UCCL - V
59681a56-b250-52e4-8772-954460f58c86 | note | Client - Su
| section | Prepour Inspection
| checkpoint | Pre pour inspection
28ff528a-118b-52b0-9c82-dbff6abeb4da | note | TEST REQUIRED - Visual Inspection
388a1272-492f-5fb0-8522-babd6d6bbde7 | note | INSPECTION BY - UCCL, MEL, WSP
de4d308d-a320-50cd-921d-9fe141f9f5e3 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing structural concrete
8ebe09fb-dce3-5cd5-87c7-c21286472733 | note | ACCEPTANCE CRITERIA - Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete.
b156ec4c-540d-5d9a-9792-5ded84a1c158 | note | UCCL - H
6f19ea62-2ee8-5326-adff-18ddb2752a51 | note | Client - W
| signoff | HOLD POINT
| section | Postpour Inspection
| checkpoint | Post pour inspection
0f87c4f1-6f31-5187-b128-3651ec9b10bc | note | TEST REQUIRED - Visual Inspection
724a37e9-0b05-5b6a-ab3f-52a2985055c0 | note | INSPECTION BY - UCCL
fb67f8f9-33f9-5c7c-82f0-e3f3c01fc721 | note | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
05a7a0de-8265-5c98-913b-55bb0bfbd896 | note | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each pour.
272c629c-97d2-544c-83ac-1fddf7c3e8ed | note | UCCL - A
f0ece2bc-9bef-57eb-85fe-1e8d39476118 | note | Client - Su
| section | Post Construction
| checkpoint | As Built & Final Design Documentation
4ab69cb8-fa7b-53ed-8cd3-aa736b9a79d8 | note | TEST REQUIRED - Surveying
b389ca5f-475a-5bd4-9ac9-ac2c941eedd1 | note | INSPECTION BY - UCCL
d79d0632-032e-5cd2-b6af-a04a969cf066 | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
894f8aab-fe5c-59b3-8156-3544dfd17eb3 | note | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
2d8a961c-1c34-5b5e-8541-9b10c1397198 | note | UCCL - S
0b50ff9b-4728-50a0-be0e-edbdb22bf649 | note | Client - R
| checkpoint | Records of:
3403217d-75a8-59fb-814b-67e91f5056e0 | note | SPECIFICATION REFERENCE - Products and materials selected for alternatives specified, Approved substitutions and accepted alternatives, Other approved changes and deviations to items specified.
245d164e-ad45-5a68-bdd3-901dda2aeeeb | note | INSPECTION BY - UCC
e3734712-a2ab-5ba1-88b3-c2f5077f25b2 | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
ac78d5f2-2a70-5ddf-bba3-9ab7f8df5622 | note | ACCEPTANCE CRITERIA - Confirmation From Engineer of all records
c50373ec-dc7f-51d8-9428-812cd6c26d7e | note | UCCL - S
3ef35ab5-da76-563c-a0a2-9925eb196534 | note | Client - R
| checkpoint | Producer statement
96ec4d67-a708-55b9-b649-4c89a4b06ca6 | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
9842e11c-b4ff-5a51-a9dd-c4a425983eea | note | TEST REQUIRED - Submit a producer statement for precast units
723d0dcc-a778-5d98-9706-0656b2481cff | note | INSPECTION BY - UCCL
0f5ca29d-62c5-5978-8c93-f4c91cdc9c7f | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
1ee6a460-bf9f-54a4-a3fd-8cac62b5145f | note | ACCEPTANCE CRITERIA - Producer statement to verify the products meet the requirements specified.
c205097f-5f10-5794-9bbe-79d786037b76 | note | UCCL - S
77398384-eb10-5406-a15c-c765197f5298 | note | Client - R
| checkpoint | Completion Inspection inc. Construction Defects Report
f7ee1f7f-2893-5b43-b468-650af138b8ba | note | TEST REQUIRED - Completion inspection on each foundation by CEL
c67cbaa4-c23b-57e8-920e-335e6b37812e | note | INSPECTION BY - UCCL
fda6f7db-8920-5b25-b095-593b9c941b7f | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
d5732374-7b88-509d-a5ba-b0bb927b8e91 | note | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
f8626187-16fa-57df-9f13-dd764053e012 | note | UCCL - S
28927bce-1a14-58e2-9cc9-5dd4a3318a30 | note | Client - R
| checkpoint | Identification of panels
b0b21fd9-849e-52d9-86ea-1616d263df96 | note | TEST REQUIRED - Panel identification location
d048a50e-758c-51af-bdf5-abdb933f6b4a | note | INSPECTION BY - UCCL
9eb1c352-0b21-5155-861c-baa51c1999d1 | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
0f8830a4-8d47-53e0-a009-0dccd2b7137b | note | ACCEPTANCE CRITERIA - Panels to be marked and identified as to which pour they're from and final location.
d7b97580-fb04-5f19-965b-0dfa0f7344bf | note | UCCL - V
832cb9ea-a5d9-52de-8e1c-d52b5f412223 | note | Client - R
| checklist | ITP 02 - Duct Installation | itp | ITP 02 - Duct Installation | 66ddc652-ca02-437f-a54a-9bd58409a887
| section | Preconstruction
| checkpoint | Review of proposed work
19b45186-6d75-5342-9519-9c8749006daf | note | TEST/TASK REQUIRED - Drawings to be reviewed and permission to proceed given.
218de57d-3f30-521e-a763-e10d57a2956f | note | INSPECTION BY - UCCL, MEL
d2b285b6-16cb-5b5d-b318-51b6a556a48f | note | TASK TIMING OR TASK FREQUENCY - Prior to Ordering Materials
f4109371-f3a2-5add-b87d-27eea2b42f31 | note | ACCEPTANCE CRITERIA - Drawings to be IFC
38cce9a1-f486-563f-8007-cb24a811262d | note | UCCL - R
402f0dee-326f-52de-a236-baa26890b48b | note | Client - A
| checkpoint | Survey Setout
840e8bf2-fb08-5520-9275-2fe3185d5a73 | note | TEST/TASK REQUIRED - Initial Setout by Surveyor
62a4440d-a3d0-5aaf-9d02-779eb0f4a1b9 | note | INSPECTION BY - UCCL
852155be-d299-556c-9c2e-90e80432f234 | note | TASK TIMING OR TASK FREQUENCY - Prior to Installation
90a78515-5437-562b-99f7-d0ab3848c4e8 | note | ACCEPTANCE CRITERIA - Surveyor to set out prior to construction
2184735e-68e9-5205-9e8c-d8de69311054 | note | UCCL - V
af316919-90b5-534b-8234-604eecec133b | note | Client - A
| checkpoint | Service Ducts
b16db5ad-c62f-5094-ae6a-8d0e834c164b | note | SPECIFICATION REFERENCE - 14.4 Specification for laying Cable Ducts
4adde750-e4a2-5360-9440-9819038aa49b | note | TEST/TASK REQUIRED - PVC Heavy Duty Electrical Ducts 50mm, 100mm and 150mm diameter. Colours as specified on drawings
51afe042-265b-528b-9514-a5236229d6f5 | note | INSPECTION BY - UCCL
8c13edf9-1f36-5b5d-adde-09f2c9e5d6ed | note | TASK TIMING OR TASK FREQUENCY - Prior to Installation
e0f585ac-c532-5cde-961b-862e861f0d17 | note | ACCEPTANCE CRITERIA - Supplier Documentation
f92b2780-9896-5fde-b110-4142318e8334 | note | UCCL - S
c39305aa-4f76-514a-9269-518ee5b3597a | note | Client - A
| section | Installation
| checkpoint | Installation of 100mm Ducts Between PCS Slab and Containers
c117f991-932a-504b-9917-c6e5604d4712 | note | SPECIFICATION REFERENCE -
d50ecbbb-9361-52d2-b7ce-182570a0a751 | note | TEST/TASK REQUIRED - Visual Inspection
62a1623a-8ff5-526a-b5a5-f0a6e44b5017 | note | INSPECTION BY - Meridian
8a03d01f-80dd-5f40-bf71-51d1d2754db5 | note | TASK TIMING OR TASK FREQUENCY - On completion of the installation of each set of 100mm ducts.
83cea5fc-c8ad-514b-a54e-ca45c6ef1571 | note | ACCEPTANCE CRITERIA - Orange 100mm ducts from PCS slab to container installed to correct line and depth.
d7aa7bb0-d757-57bb-8aa9-4a184afc0f98 | note | UCCL - V
f9729028-0964-503d-a2e5-54d9c4aaabc6 | note | Client - A
| checkpoint | Installation of 50mm Ducts Between PCS Slab and Containers
5a6b7ca5-f404-5212-abf5-48846f0eb1c3 | note | SPECIFICATION REFERENCE -
ef5fd480-57cb-538d-a32a-0138df4a68b8 | note | TEST/TASK REQUIRED - Visual Inspection
7f8f88d2-b2ab-5420-9507-846e26036b97 | note | INSPECTION BY - Meridian
50e1fd72-33fe-529f-9d54-ce73dcfba3c6 | note | TASK TIMING OR TASK FREQUENCY - On completion of the installation of each set of 50mm coloured ducts.
1315dd27-e083-5622-936b-2464c1bf5328 | note | ACCEPTANCE CRITERIA - Coloured 50mm ducts from PCS slab to containers installed to correct line and depth.
cb2d71bb-31a9-5424-b04a-1ae4d7f20436 | note | UCCL - H
e2cc7b5e-dbaf-56e8-a38e-5128c54415ab | note | Client - V
| signoff | HOLD POINT
| checkpoint | Thermal Backfill (as directed by principal)
68e7ace7-d091-52aa-af2b-af26aba6d9de | note | SPECIFICATION REFERENCE - Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265
4997e250-544f-5d09-8f23-ee930bb2bad8 | note | TEST/TASK REQUIRED - Visual Inspection
27b674e0-85ab-569c-a8e0-e80932a4d2fd | note | INSPECTION BY - UCCL
0d5c5cdb-61df-50b1-98d9-796ec70df0eb | note | TASK TIMING OR TASK FREQUENCY - Following instalaltion of ducts, where specified
37e5119d-f239-57f3-a46f-ab1d5d819aa2 | note | ACCEPTANCE CRITERIA - 10 passes with plate compactor, per MELNZ-RFI-000310
15126df3-8a05-5c11-982c-27d6396a77ff | note | UCCL - V
7c291a3f-daee-53fe-b244-d8fc8b83e983 | note | Client - A
| checkpoint | Sand Backfill
71f2c402-a26d-5b40-a2b6-ecd41ee7530b | note | SPECIFICATION REFERENCE - Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265
2403c26f-2955-519c-b6eb-a0b1c5d3922f | note | TEST/TASK REQUIRED - Visual Inspection
3ecb5d4d-9709-5be8-8057-f4bfeb2c22e3 | note | INSPECTION BY - UCCL
7df97b0b-f90c-551e-86ed-f3ec46ed37df | note | TASK TIMING OR TASK FREQUENCY - Following installation of ducts, where specified.
e9dc6948-ae60-5968-9673-277f8e727455 | note | ACCEPTANCE CRITERIA - Self compaction of sand, as per MELNZ-RFI-000310
50d46d35-cbda-5783-b891-dc205c3a2b24 | note | UCCL - V
9488f4cb-ad96-5358-9813-68ad5abd50f1 | note | Client - A
| checkpoint | Flowable Fill
9982be00-2157-59a7-8f02-426fd358a7a0 | note | SPECIFICATION REFERENCE - Refer MAIL NUMBER MELNZ-RFI-000393 (Ducting at 101A, 201A, 301A, 401A and 501A requires flowable fill as per drawings supplied)
70049592-e885-5ab1-bcc8-e3d6d99693a5 | note | TEST/TASK REQUIRED - Visual Inspection
e488808f-1c59-5bdc-9179-48f0edaee540 | note | INSPECTION BY - Meridian
1c1990e5-eef3-5ca9-a487-1745349f4d81 | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring flowable fill over 100mm orande ducts at 101A, 201A, 301A, 401A and 501A.
661c4b0d-7ab6-5c52-9ade-b62c420ddc58 | note | ACCEPTANCE CRITERIA - Orange 100mm ducts from PCS slab to container installed to correct line and depth. Ducts braced and height pegs set for correct cover.
805fa291-4cae-56c1-b7e2-fdc0b5da18c6 | note | UCCL - H
f8bd0dda-0fee-5f10-9228-7ff49a4dce4d | note | Client - V
| signoff | HOLD POINT
| checkpoint | AP40 Hardfill Layer
46db4cc0-abc2-5397-af54-01be9e9fe3db | note | SPECIFICATION REFERENCE - Construction Drawing Set RUK-UMC-DS-01. Also refer MAIL NUMBER MELNZ-CA-000290.
c757b580-7054-5f54-956d-cb65d723ba43 | note | TEST/TASK REQUIRED - Visual inspection. Cleeg test with minimum CIV value of 25.
c8972f7c-63dc-5fc6-8678-d27e2ae4222c | note | INSPECTION BY - UCCL
04070ed6-58f7-5f73-beab-ed9d164565cf | note | TASK TIMING OR TASK FREQUENCY - On completion of AP40 hardfill layer, prior to site concrete.
37d00198-5930-5516-a75e-5d34991ea1a1 | note | ACCEPTANCE CRITERIA - Minimum CIV of 25.
ec207812-f7a0-55a3-9d06-c0b566546dd2 | note | UCCL - V
5e805e68-42af-54b7-985b-f61eb5f50227 | note | Client - A
| checkpoint | Cable Pits
9d20f8da-2741-565d-a3c1-a51f9c5a59b1 | note | SPECIFICATION REFERENCE - 14.4 3 Specification for laying Cable Ducts
fde25a45-882c-5796-8c08-3ee9410f2319 | note | TEST/TASK REQUIRED - Supplier Documentation
f68b94ad-aad9-55c1-91c4-6c5762d20bad | note | INSPECTION BY - UCCL
bd56e39e-cca7-560c-ba90-1063e55cbbcb | note | TASK TIMING OR TASK FREQUENCY -
a6ccb820-78bc-530b-ba97-b520ced0e315 | note | ACCEPTANCE CRITERIA - Cable pull pits to the dimensions shown on drawings
ddc1a157-d1fd-50c1-a0eb-be0244dd9d7f | note | UCCL - V
9a319dcb-613f-5d96-a9bc-07299305fab5 | note | Client - A
| section | Post Construction
| checkpoint | As Built & Final Design Documentation
5b9bf436-8f3d-5df9-9d05-e3ed77ba249d | note | SPECIFICATION REFERENCE - 14.4 2.3 Specification for laying Cable Ducts
5755a341-c9cc-59ce-b3e7-1a5c57639370 | note | TEST/TASK REQUIRED - Surveying
e5bc8bd3-8deb-57ba-9536-63983667f995 | note | INSPECTION BY - UCCL
19433b00-4177-5d5f-a6c2-d2214a845e60 | note | TASK TIMING OR TASK FREQUENCY - As constructed
1f45c529-314a-5277-a42c-99b4ccf714dc | note | ACCEPTANCE CRITERIA - The contractor shall undertake site survey of all duct ends so that they are installed within +/- 15mm of their design location
2084e0e1-3f6d-519e-b341-090c68a44d30 | note | UCCL - S
1b48e617-f81d-59c4-aba0-70759f46bf1d | note | Client - A
| checkpoint | Ducting QA
b0d6c845-638b-584f-9090-d5cb9961c640 | note | SPECIFICATION REFERENCE - 14.4 Specification for laying Cable Ducts
a2cf2432-8b84-5b4a-a02a-d34fac590dac | note | TEST/TASK REQUIRED - Duct Inspection Record
583a149f-5634-518d-a1f5-8630fc6bb315 | note | INSPECTION BY - UCCL
9532d9f1-2089-57b5-a24e-e50336f5adc4 | note | TASK TIMING OR TASK FREQUENCY - Per trench
67201a61-e3d2-588b-bf18-a57843728013 | note | ACCEPTANCE CRITERIA - Duct Inspection Checklist completed per trench
78d6f769-8dd1-5088-bb2a-c37495b9c85c | note | UCCL - S
53e3ead3-488b-5fbf-8433-4c9b843debb4 | note | Client - A
| checkpoint | Completion of Ducts for Handover
0c1e541f-3761-5239-b7c8-83a71f9bb288 | note | SPECIFICATION REFERENCE -
f59428f3-ecb2-5875-85ff-1636587cc284 | note | TEST/TASK REQUIRED - Handover Record - Handover of Ducts to Electrical
4eecca87-9070-57b2-a825-e111cc48a8f9 | note | INSPECTION BY - UCCL
f37185ee-5ae0-5817-89fe-6d6f4876262d | note | TASK TIMING OR TASK FREQUENCY - On the completion of duct installation at handover for electrical installation.
d7032c2d-38f2-50a3-ac2d-bb808f809c25 | note | ACCEPTANCE CRITERIA - Handover record sign by UCCL, Meridian, and Electrical Department. Ducts installation completed, and ducts cleaned ready for electrical installation.
aa39da1d-adc2-5be4-9f08-ccdf759138fc | note | UCCL - H
eca05d81-670e-5dfc-85ad-502c9918924a | note | Client - V
| signoff | HOLD POINT
| checklist | ITP 03 - PCS Slab | itp | ITP 03 - PCS Slab | aeca5c6e-38c3-42e4-bd9c-30089000fcdf
| section | Pre Construction
| checkpoint | Site Concrete
548c549a-c655-5254-bf01-5d4419664d21 | note | TEST REQUIRED - Visual Inspection
01daf045-2aef-562f-994e-cb642d016fef | note | INSPECTION BY - UCCL
9ff9fb3a-9dd6-5f16-88a0-2f663a8d1410 | note | TASK TIMING OR TASK FREQUENCY - Prior to survey setout
51e4fbd1-5946-599f-bc16-11f62f41517f | note | ACCEPTANCE CRITERIA - Site concrete at correct level, and surfacewithin accepted tolerances (+/- 10mm).
632d5e0f-fc2d-5d57-9163-921667b1695c | note | UCCL - V
| checkpoint | Survey Setout
a75d88da-87a5-5b18-9aa2-f27a71a18fbd | note | TEST REQUIRED - Surveyor to set out PCS slab including duct recesses and bolt positions
910d0472-52c0-5495-a5f2-12bf558c7036 | note | INSPECTION BY - UCCL
bf94ceda-70b5-5163-802d-59202d41f71d | note | TASK TIMING OR TASK FREQUENCY - Prior to steel reinforcing and formwork construction
1990a35a-49a5-514e-a40f-b436e0e6e8e1 | note | ACCEPTANCE CRITERIA - Foundations shall be set out as per IFC drawings.
bb33a783-e4d7-59cc-88e7-9ca8c65f9fbf | note | UCCL - V
3b76b207-57c2-5fb0-ba4e-ed65d83d4b59 | note | Client - W
| section | Materials
| checkpoint | Concrete Mix Design
900f05ef-a280-57b6-9ee8-50204f1aa80e | note | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
437d0a96-0679-55a3-bb93-175698b4446f | note | TEST REQUIRED - Mix Design to be approved by Meridian prior to use
7db023be-9aff-546c-8d97-4d55ea1d248f | note | INSPECTION BY - UCCL/MEL
97e745b1-e5b6-587b-b4e4-676912e9cde1 | note | TASK TIMING OR TASK FREQUENCY - Prior to use on site
934f6e07-d465-58fe-b06a-b662a761154f | note | ACCEPTANCE CRITERIA - Mix Deisgn as per specification (30MPa, 19mm) and approved by Meridian.
71212b38-6d9f-53fb-a7dd-974f3deb69a5 | note | UCCL - S
912be43e-6c88-57f7-be16-6b750cbc3d72 | note | Client - H
| signoff | HOLD POINT
| checkpoint | Steel Reinforcing
8b9944d7-87fe-50f6-92a7-59b037d3c60b | note | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
50a5bb06-f314-548c-992b-c14f222a983d | note | TEST REQUIRED - Supplier documentation, photos
9fdd2695-d218-52d6-8d21-9cc29c88364b | note | INSPECTION BY - UCCL
5ed1e12c-c08a-5e79-a955-d6d3cf27890b | note | TASK TIMING OR TASK FREQUENCY - Prior to
fe24aae6-e356-5615-89a5-ecbf13c6f0f0 | note | ACCEPTANCE CRITERIA - Steel reinforcing comlies to specifications/IFC drawings/
1e058c7b-f958-5e51-af06-b963338c80b2 | note | UCCL - V
897e3832-9b97-5981-828e-b0ac51bf2fdb | note | Client - W
| section | Prepour
| checkpoint | Formwork
39c6bcce-1913-5bcb-a2a0-4ed7981d5630 | note | TEST REQUIRED - Visual Inspection
9a9214d2-4e5e-577b-b676-3b1a977834df | note | INSPECTION BY - UCCL
47d39af0-f1cc-556b-a5b4-5ca6035e2428 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
f59813a7-54f4-515a-a4ca-00617856520a | note | ACCEPTANCE CRITERIA - Dimensional check completed and within tolerances. Formwork installed inspected as being suitable for pouring concrete.
5c099c12-895b-5984-ae09-dc10d8e8cb2f | note | UCCL - H
79e5ca58-454e-5cb7-b273-3d580a496d75 | note | Client - H
| signoff | HOLD POINT
| checkpoint | Steel Reinforcing
1f316256-c6a0-5a67-8050-d068acf93512 | note | TEST REQUIRED - Visual Inspection
f5756a2e-fc0b-5455-aa84-87096bbd91bb | note | INSPECTION BY - UCCL/MEL
972f4e25-cf5c-5adf-afec-7ca3bb9c850b | note | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
b2df2c30-3171-5b31-b738-724dfe55e4d8 | note | ACCEPTANCE CRITERIA - Steel installed as per IFC drawings. Grade of steel as specified. Number, size and spacing of bars as per IFC drawings.
eea9c98f-7189-5c7d-b768-c99dcde196c0 | note | UCCL - H
b7f854d2-ec4e-5c32-9fc3-dc1154408b79 | note | Client - H
| signoff | HOLD POINT
| checkpoint | Foundation Earth
f8f76a17-e534-5bfe-8509-18daa0556d21 | note | TEST REQUIRED - Visual Inspection, Continuity Test
ef44eeab-bfce-5af3-9dcc-a9b98f044ecc | note | INSPECTION BY - UCCL, MEL
350a3066-c3dc-511d-adbd-dfaf7ed1d6a2 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
a6475906-4ed7-5041-a4d8-f5821eed75b7 | note | ACCEPTANCE CRITERIA - Earth bars and cables installed as per IFC drawings. Continuity test completed and passed by MEL.
55fe623a-4bc6-5f15-a212-7b30bcd39ce5 | note | UCCL - H
f91db076-c9b2-5de4-bc0f-de361d6840ef | note | Client - H
| signoff | HOLD POINT
| section | Postpour
| checkpoint | Post pour inspection
6301610f-f7c7-5206-ae94-23b1af4408ea | note | TEST REQUIRED - Visual Inspection
ec44cbcd-0672-55a6-b1cb-a533896e8698 | note | INSPECTION BY - UCCL
c882042f-bdbd-518f-af24-d3cabdbc8d7a | note | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
2a5ac873-1cde-5e5c-93b5-e74bc19a85d9 | note | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each PCS slab pour
96a97802-9684-565d-9ea7-38b8b01b9acb | note | UCCL - A
0a7794c4-cbb0-5559-95f5-bc9d25922492 | note | Client - W
| section | Post Construction
| checkpoint | As-Built Drawings
085488ec-eef6-5daf-8b8d-7d8d4ec01461 | note | TEST REQUIRED - Survey as-nuilt drawings
54bf8e27-97eb-505e-8938-4b91aaf8cda8 | note | INSPECTION BY - UCCL
52a9858a-365a-538a-b228-901e9455742b | note | TASK TIMING OR TASK FREQUENCY - On completion of Separable Portions
507e1e66-4f8c-5403-996a-29f6da1a3e2d | note | ACCEPTANCE CRITERIA - As-built drawings submitted to MEL.
95c2a4f3-0b40-5fb8-86cd-9780923b8738 | note | UCCL - S
7268b7b9-37a7-5f18-a0ad-9d93a076c527 | note | Client - R
| checklist | ITP 04 - Platform Pavement Layers | itp | Platform Pavement Layers | ae6b092e-0cae-4542-8b5e-873ccde3d13b
| section | Platform Pavement Layers
| checkpoint | 1 - Subgrade (Existing Brown Rock Surface)
7fb12a53-e4f2-5809-b3f0-b3306cdc96d1 | note | SPECIFICATION REFERENCE - Civil Works Specification Section 2, Clause 14.1
ef1ac296-4437-5bc6-8ec1-e86497228a66 | note | ACTIVITY/TASK - Proof Roll Witnessed by Principal's Representative.
fcddb9f6-7b76-53d4-af3d-30fbe5c77ec9 | note | INSPECTION BY - UCCL/MEL
d27c95c5-54ac-5bca-a890-2d2916051253 | note | TASK TIMING OR TASK FREQUENCY - Prior to commencing with the AP65 subbase layer.
83ee3e0f-836a-5ce6-81e4-cb2106d8c5ba | note | ACCEPTANCE CRITERIA - Acceptance of subgrade by Principal's Representative.
c807a04f-43c2-577e-a048-2de9c8fcaf60 | note | UCCL - H
9557ed86-b43a-51a6-83ea-8ee46dce42ee | note | CLIENT - H
| signoff | HOLD POINT
| checkpoint | 2 - Subbase Course Material Testing
28691a17-a2e5-55d6-8d90-8eef2bd02f53 | note | SPECIFICATION REFERENCE - Civil Works Specification Section 2, Clause 14.4.2
3facf9da-c087-59c9-8671-78d43e3393aa | note | ACTIVITY/TASK - Material Test Certificates
4a789a52-33d7-5fcd-9e89-e864f6131669 | note | INSPECTION BY - UCCL/MEL
b63ecaa8-2c06-5506-bef6-a14dae07f9c3 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing AP65 subbase layer on site.
2ef83ee9-b192-5660-8727-7b6f85673cc9 | note | ACCEPTANCE CRITERIA - Material meets specification. Material acceptance by Principal's Representative.
6374f923-d63b-5a1d-9741-c7041c56af87 | note | UCCL - S
ff4d8528-0c1a-5279-8296-ec1488178d39 | note | CLIENT - A
| checkpoint | 3 - Subbase Compaction (Under Containers)
d5fe8688-ddf0-56fa-bf4b-8dcb598dfea9 | note | SPECIFICATION REFERENCE - MELNZ-CI-000133
1e1f5c0b-a7e1-53b9-9d29-69923b5f7407 | note | ACTIVITY/TASK - Clegg Testing - Minimum Clegg Impact Value (CIV) of 25.
db3ed401-c3d8-562c-bcbb-c51604608b48 | note | INSPECTION BY - UCCL
0abba543-ecb9-58c5-8c84-bcc07c7c6f4a | note | TASK TIMING OR TASK FREQUENCY - Prior to placing Fibre Concrete under containers. Minimum 2 tests under each container.
3593ddbc-447b-515f-a2b6-0c95a75ce72b | note | ACCEPTANCE CRITERIA - Minimum CIV 25 achieved. Acceptance by Principal's Representative.
366c7155-282b-5bdd-afff-b354fae44346 | note | UCCL - W
9f9e6e30-68fa-5713-ad07-05ed32be667c | note | CLIENT - W
| checkpoint | 4 - Subbase Compaction (Inner Zone Between Containers)
867fef1d-3c2b-573d-aa96-ef3d2881edeb | note | SPECIFICATION REFERENCE - MELNZ-CI-000133
3bd6eadb-e729-54ed-b626-31206ab39021 | note | ACTIVITY/TASK - Clegg Testing - Minimum Clegg Impact Value (CIV) of 25.
60b1f73a-74fd-58e0-8a07-173cbc2028fb | note | INSPECTION BY - UCCL
731edb47-446b-598f-a3d6-307528380734 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing Basecourse layer.
78c115dd-027c-53d0-8b60-a36d94e1d45f | note | ACCEPTANCE CRITERIA - Minimum CIV 25 achieved. Acceptance by Principal's Representative.
5adccc31-25be-52b5-a8a6-a1ff15d59d6a | note | UCCL - W
79b355d2-ef76-593a-adc4-6079d2cddc44 | note | CLIENT - W
| checkpoint | 5 - Subbase Compaction (Site Roads Outside of PCS's and Containers)
75035689-7469-58b6-9174-bf1001d35be9 | note | SPECIFICATION REFERENCE - Civil Works Specification Section 2 Clause 14.4. TNZ B/02 Clause 7.6
fff69a16-772d-528c-b582-9b4658372703 | note | ACTIVITY/TASK - NDM Testing
f2d4b35c-83e7-5542-a392-1ee1c6d110f1 | note | INSPECTION BY - UCCL/MEL
f146cbf6-8842-5a1e-984a-64943963facd | note | TASK TIMING OR TASK FREQUENCY - Minimum 5 No. NDM Tests per area. Compaction to achieve average > 95% MDD with minimum value > 92%.
f55e882e-061a-5789-85ff-a357159cadf6 | note | ACCEPTANCE CRITERIA - Compaction achieves average > 95% MDD achieved with minimum value > 92%.
27afc662-1e1a-57f1-aa35-3d837daafb86 | note | UCCL - H
5e8b59f1-b23a-57d2-b506-add10e269365 | note | CLIENT - H
| signoff | HOLD POINT
| checkpoint | 6 - Subbase Tolerances
94fc93a7-89d0-563d-a2aa-15a7eab7d05b | note | SPECIFICATION REFERENCE - Civil Works Specification Section 2 Clause 14.4. TNZ B/02 Clause 5.1
e680ae5b-9523-5f48-9d01-d5ac050699a4 | note | ACTIVITY/TASK - Strings. Survey setout/as-builts.
a0eaea09-199d-5977-bdee-2bffedd31397 | note | INSPECTION BY - UCCL
183ca915-0878-5403-8d03-66658935b63a | note | TASK TIMING OR TASK FREQUENCY - On completion of Subbase layer prior to placing Basecourse layer.
b73d1429-58ba-59ac-8ef1-3340d18778f1 | note | ACCEPTANCE CRITERIA - Line and level within tolerances.
499cc5fb-b8f7-5d4d-936f-f1f17c349948 | note | UCCL - S
4b52e17c-6927-55de-8478-f36ed2fe5f4e | note | CLIENT - A
| checkpoint | 7 - Kerb and Channel
fdc5e1b1-6ce8-5856-a5d5-747290bbc65d | note | ACTIVITY/TASK - Kerb and channel installation
0c287bda-92c5-5e50-87a7-c8e28116872f | note | INSPECTION BY - UCCL
2a409824-15c0-50a4-a97b-9a403c305c69 | note | TASK TIMING OR TASK FREQUENCY - On completion of kerb and channel installation.
be05f294-f271-5d19-9199-2de198b250c6 | note | ACCEPTANCE CRITERIA - Kerb and channel meets specification.
1ac3a220-292a-5857-94ce-7b65d42a9cb1 | note | UCCL - W
c6191505-9cc3-5d66-88b3-5593735d9a54 | note | CLIENT - W
| checkpoint | 8 - Basecourse Material Testing
50832efc-15d5-5fbe-8ab7-a5ecf72e9c45 | note | SPECIFICATION REFERENCE - Civil Works Specification Section 2 Clause 14.5.
2d055aaf-9b5d-51cf-92e2-cbbc24282bf1 | note | ACTIVITY/TASK - Material Test Certificates
04a2ab1e-49b3-5297-ac43-e897ddda27b6 | note | INSPECTION BY - UCCL/MEL
69182132-2abb-5616-94da-0eec2b475944 | note | TASK TIMING OR TASK FREQUENCY - Prior to placing AP40 Basecourse layer on site.
633a0769-bdd6-5d26-8edc-bf9d70382e61 | note | ACCEPTANCE CRITERIA - Material meets specification. Material acceptance by Principal's Representative.
893c75ce-1c3a-5db0-ae05-0d81278693d9 | note | UCCL - S
63a63a8f-593b-5f50-9c13-1aa0d6d6330d | note | CLIENT - A
| checkpoint | 9 - Basecourse Compaction Compaction (Inner Container Zones)
3b1b342f-d6ee-50ef-b6f5-95daf2a731b1 | note | ACTIVITY/TASK - NDM Testing
d7538a05-c507-5f8a-85bc-182de99bb5ca | note | INSPECTION BY - UCCL
f09b7030-9f64-5952-b061-445777bf2cca | note | TASK TIMING OR TASK FREQUENCY - NDM Testnig each area. Compaction to achieve average > 95% MDD with minimum value > 92%.
9ebb1b7f-ecc1-5828-9ef8-0b00e457fa4d | note | ACCEPTANCE CRITERIA - Compaction achieves average > 95% MDD achieved with minimum value > 92%.
640b84d9-abbe-501e-9c3e-fae885d04048 | note | UCCL - W
3973a3e8-6c62-561d-9bf5-9a009d3edd0b | note | CLIENT - W
| checkpoint | 10 - Basecourse Compaction (Site Roads Outside of PCS's and Containers)
835a72fb-8f71-5a73-a48a-55f8a5d86736 | note | SPECIFICATION REFERENCE - Civil Works Specification Section 2 Clause 14.5. TNZ B/02 Clause 7.6.
b0b18254-75fc-5d6e-a0e1-2585e0d76607 | note | ACTIVITY/TASK - NDM Testing
4f011e85-4b66-55a4-97dc-21f2666a07fc | note | INSPECTION BY - UCCL/MEL
53a1da76-2c6d-5b21-95e1-c2515b052133 | note | TASK TIMING OR TASK FREQUENCY - Minimum 5 No. NDM Tests per area. Compaction to achieve average > 98% MDD with minimum value > 95%.
543809ed-85ee-5b4c-b84a-057ef9cfff83 | note | ACCEPTANCE CRITERIA - Compaction achieves average > 98% MDD achieved with minimum value > 95%.
df7ab8b0-b6f9-59bb-b983-f5ecbaaf9233 | note | UCCL - H
ff0ea1f4-5512-5938-a2fa-ae9e1443fecc | note | CLIENT - H
| signoff | HOLD POINT
| checkpoint | 11 - Basecourse Tolerances
6e1bb282-a470-5c7d-be3f-1df1150408a3 | note | SPECIFICATION REFERENCE - Civil Works Specification Section 2 Clause 14.4. TNZ B/02 Clause 5.1.
bf4a3d87-e3dc-5cd5-92a3-d18824ae823e | note | ACTIVITY/TASK - Strings. Survey setout/as-builts.
7c35aacf-65e7-5f20-a824-51308cd29603 | note | INSPECTION BY - UCCL
862de067-cff3-5428-bfed-adbd822faa93 | note | TASK TIMING OR TASK FREQUENCY - On completion of Basecourse layer prior to placing Basecourse layer.
c3535ba6-f94d-57f7-8b81-7e4da277dfce | note | ACCEPTANCE CRITERIA - Line and level within tolerances.
1ad7fee8-e476-5b4b-9e18-929bbee0d70f | note | UCCL - W
d5d919a7-916b-553f-bf4b-ef84339ca255 | note | CLIENT - W
| checkpoint | 12 - AC Material Specification
9e5dd80b-3f2d-594b-9a94-656ae51049c7 | note | ACTIVITY/TASK - Specification as agreed between Principal and Contractor.
2bd41b02-fbe5-58f0-893d-f34c9cb6fcaa | note | INSPECTION BY - UCCL/MEL
ac08cede-017a-5160-aa8c-a08596c0844c | note | TASK TIMING OR TASK FREQUENCY - Prior to using the material on site
71d08a84-2b13-53ba-85fc-4991ea641791 | note | ACCEPTANCE CRITERIA - Specification as agreed between Principal and Contractor prior to works commencing.
ac6544bd-ef13-580a-92e9-bcfe37d434b7 | note | UCCL - H
6dd24f65-503a-5a48-962e-ae0e9b5af341 | note | CLIENT - H
| signoff | HOLD POINT
| checkpoint | 13 - AC Pavement Testing
6de8850d-8b74-5d8e-89af-38bccba44be7 | note | ACTIVITY/TASK - Testing as agreed between Principal and Contractor.
a56f8f7b-3bbc-5489-a97d-a31a5ae7a2fa | note | INSPECTION BY - UCCL/MEL
b7a8f1f8-603a-53fb-9a90-cc3327aa3b8a | note | TASK TIMING OR TASK FREQUENCY - On completion of AC pavement layer.
283c95f2-ec5d-53a0-a77a-fd18ba2b5103 | note | ACCEPTANCE CRITERIA - Testing as agreed between Principal and Contractor prior to works commencing.
58ee7be6-3738-52f4-94c3-b20d47c07765 | note | UCCL - H
5edbaf3e-0ca9-511b-b574-7a6ab76b3f96 | note | CLIENT - H
| signoff | HOLD POINT