## Master List Templates
Id | Type | Name | Values | Prompting Name
7869787a-85ae-41b0-9e69-a7134de9ae5c | checklist | ITP 001 Hydraulics – Cold, Heated Water & Recycled Water |  | ITP 001 Hydraulics – Cold, Heated Water & Recycled Water
91421ee2-9532-4c58-89ed-f37e27ea7f78 | section | Scope of work
351c0965-e643-40db-ab3b-1dc531e8d412 | checkpoint | Check documents are current & for construction
c449511b-5e7e-401e-948b-c8ab1b940192 | checkpoint | Check levels & falls
9fd6ed5f-536f-4b22-b511-39e55bad0ab4 | section | Competency
6b76684b-1e18-43c8-9575-d44c309b68a1 | checkpoint | Trade Registration
a8c1ded9-ada5-46d9-912f-0bc1199f1d28 | section | Set Out
d54a94a0-6858-427f-b2a5-c5ddb7ef02a8 | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
6b38bb07-6b41-49e1-8e71-96fe5d0d84e6 | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
58ec85de-6aae-4c05-8319-88a9a92ed9e8 | section | Pipes Support
72bc3008-a770-4d3b-8b1f-67a11af6f608 | checkpoint | Pipes to be supported as per AS 3500. Extra supports to be added to prevent pipe movement caused by water pressure effects
8f53fbf0-00d4-4e0a-bc17-eca799f34220 | section | Valves
b67a19a8-5be9-4b4b-bb9f-8897fe921c45 | checkpoint | Check valves for water mark approval.
d951f268-4a4c-48da-8f42-acf376c26b35 | section | Piping
49893e1c-2ba0-4d95-91af-2389defd708c | checkpoint | Pipework sizes as per for construction drawings.
4475be6d-4fff-4fd7-be17-d4a2e260492e | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
7c4d35c0-24ae-4a25-8e3e-110ff3f61929 | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
1fca1e77-cbe0-4780-b7c5-5e27cfba0701 | checkpoint | Minimum separation of underground services is achieved
0aa90ee4-dc76-4de0-a8d5-923e461d9d73 | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
afcc203c-5423-46b8-84a2-51150330b12a | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
4dbba29d-594d-4d82-9036-897bd142f092 | checkpoint | Penetrations are of suitable height and have been capped where required.
a868b74a-5b3b-4c71-9b2d-36cbe487a87d | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
edce40d6-1cf7-4990-a885-ec9232278e9d | checkpoint | Pipework have been installed without damage
bff547f4-f963-4999-bf3c-eeda222a0cd3 | checkpoint | Pipework Joints have been appropriately treated/glued
6a6b591c-f8cd-441a-b302-9e2c254b6e32 | checkpoint | Pipe/conduit compliance record/certificate
a4c5efda-ce5b-47f5-9aa5-f84b6c224d9c | checkpoint | Thrust blocks installed as per detail
9e0bb06b-4264-4e87-9cf1-e95dd1b3fd8d | checkpoint | Protruding services have been adequately protected from future construction damage
7c440128-9bc0-4899-81ba-09dfd9f8dd6f | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
bdfd29b0-0a33-4006-b029-150f36abef8b | section | Insulation
3ca9bd09-3fd7-44c8-aa24-00af95d7953b | checkpoint-no-value | Insulation
8c610b3a-dd00-5b56-a25f-7440db2202b0 | note | Specifications, design documentation and issued for construction drawings
ac30d6a2-8e13-477a-809e-2d2ebb4101a2 | section | Marking & Labelling
4c44694a-849f-402d-988b-406475427f9f | checkpoint | Underground pipework to have identification tape installed.
1047d85c-e717-4e27-ade8-470ec6c8b80a | checkpoint | All marking tape is in accordance with Australian Standards
0ba5cde1-d03f-412b-83ec-30330d61f944 | section | Pits
1e19be74-b986-4372-86c1-ca03b0ce5012 | checkpoint | Specifications, design documentation and issued for construction drawings (AS 3500)
a44105bf-63a3-4280-a035-438ed3399e68 | section | Testing
4afeebe0-c5fd-4805-ad07-341d62c513b0 | checkpoint | Prior to testing the system shall be flushed of all foreign matter. Hydrostatic pressure test before backfilling, lagging & covering. Pipework with elastomeric or RRJ shall be backfilled leaving the joints exposed. Test as per AS 3500.4. 1500 KPA for 30 min. No leaks are acceptable. Some fixtures cannot handle 1500 KPA.These items are to be disconnected for the 1500 KPA test then reconnected and tested at their maximum operation pressure for 30 min
42473314-c422-4e88-8777-6feac896e08b | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
a111459b-e42e-420a-8a32-c6982061e64c | section | Backfill Compaction
e1a7ee1f-3779-41e7-8125-d7c2c2dabd40 | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil Photographs of installed services prior to backfill Bedding material is in accordance with the IFC drawings, sample submission and specification Bedding material grading certificate to be provided Trench backfill material is in accordance with the IFC drawings, sample submission and specification
de04176a-33e5-4f55-8336-276bdda6479f | section | Final Trim / Clean Site
60d1b030-d33f-495f-91e4-445d91105651 | checkpoint | Final clean and grade site area affected by the water services scope of works. Excess spoil removed in accordance with terms of contract
78f5d5d2-c15b-4fb4-bcce-d97123847393 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
29aa1bb8-aa02-423f-b9d7-83ada85b1291 | section | Final Inspection / Completion
fc76c40c-7bac-4fd4-b2f8-1c31a06ac111 | checkpoint | Verify all inspections, complete records. All Authority approvals have been received with Supporting records from Services Subcontractors
ee106c87-80a2-4049-9159-061af0ce22d7 | section | Record Drawings
827af666-493a-4cf8-b753-944b2943132d | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
b4c5ba63-23b7-4b81-8040-c682c7510b75 | checkpoint | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
2910ba5f-5a53-438b-a28c-1dbf9a7ec927 | checklist | ITP 002 Hydraulics – Fuel Gas |  | ITP 002 Hydraulics – Fuel Gas
14c1c626-4af8-44e1-b973-58136a32ebf1 | section | Scope of work
26deed8c-b058-4f44-9553-2b95d0916905 | checkpoint | Check documents are current & for construction
8dbcfc88-0bfa-4633-aeae-7ab87ccfd3b8 | section | Competency
9edc8b15-3c45-42c4-a87a-b9225a52fc25 | checkpoint | Trade Registration
2bb1d0dd-c8a6-4fc9-9e07-75fe410689da | section | Set Out
9d38f678-31b2-4808-a88c-3051d52c23ac | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
dfb49984-09af-4029-a94a-4651742155bb | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
c5d3e4a9-65d9-487b-82b8-1a15cccea46e | section | Pipe Support
5b3741f6-8311-4957-b8ee-b20b344fbee8 | checkpoint | Pipes to be supported as per AS5602 clause 4.3 tablet 4.2 & 4.3
83dd20c8-3d63-4b7a-9da4-bddb76c44ecd | section | Piping
5734bbcb-2966-44d2-9d1b-e2fd142142f6 | checkpoint | Pipework selection and sizes as per for construction drawings.
625a701e-1520-4b4c-bf7f-379e82f1f48e | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
d64c4437-1762-4459-8f26-155558ec4d9e | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
aeeddac7-e149-4b6e-bd7a-a732d690b33a | checkpoint | Minimum separation of underground services is achieved
10470926-09c3-42ac-805e-7df7028f988a | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
bf9b50f9-c389-43ac-8262-8db21c9e496f | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
922a5485-ecf0-4887-8107-1ef036afbc7c | checkpoint | Penetrations are of suitable height and have been capped where required.
f12ba421-e6e2-4ef2-8afd-cd87cf3a255d | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
d499a6fe-d684-4cc8-b09c-d0a9ddb8a950 | checkpoint | Pipework Joints have been appropriately treated/glued, Pipeworks have been installed without damage
71756427-f6c1-41b1-bef9-f19e0ae50f64 | checkpoint | Protruding services have been adequately protected from future construction damage.
7fd871fa-02dd-4120-810b-5bc553708e15 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
3e45749c-824e-40a0-b299-991ab1a1a921 | section | Valve Boxes
6f942536-93db-4bb1-a0a4-42afc7a6f23b | checkpoint | As per specifications and for construction drawings
ef17acd3-5ce7-4d41-811c-cf32a08edea1 | section | Marking & Labelling
3e798f40-f068-4faa-bcbe-1af660f12516 | checkpoint | As per specifications and for construction drawings
6743b447-8e41-4af4-8928-c159e8999c0a | checkpoint | All marking tape is in accordance with the Australian standards
6dceae69-fa62-4790-916a-b214b009e9e5 | section | Pits
8fa5f0da-6e71-4720-a58e-fa4b1a05dac5 | checkpoint | As per specifications and for construction drawings AS5601
87f251d4-95cc-4d08-be91-127a7a93aff9 | section | Testing
f7cedd5f-1632-425e-946c-20b74b9a1e06 | checkpoint | Prior to testing the system shall be purged of all foreign matter as per AS5601 clause 2.4 & App. D
22737592-c712-4d31-b876-9baadd22a705 | checkpoint | Testing to be undertaken prior to the connection of appliances
8d1cacc0-7488-4655-8d3f-24cd5b5ebfc1 | checkpoint | Testing of service as per AS5602 Appendix E. Pipe work to be tested to 1.5 times the operational pressure
4e5fc2ee-74ef-49fb-a0de-06890bf30ad1 | checkpoint | Inground services have been inspected by the relevant authorities/consultants prior to closing up (witness/hold point)
4825e286-c841-446b-a923-74116b658d60 | section | Backfill Compaction
1cb5e70b-00b6-4d9a-a1fe-758ea95f2ca4 | checkpoint | Photographs of installed services prior to backfill
176a65b0-4c05-4334-ab3a-a5d35768ec4a | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil
1877aa12-abb7-47ad-a150-7ab5da9ff356 | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification
9e51fc31-cadf-4340-aa5d-4173c5e676ef | checkpoint | Bedding material grading certificate to be provided
82c9b4af-d378-461d-a1e7-41ba6082d1f8 | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
03c90b03-36e2-4dd7-99db-92636968a7b7 | section | Final Trim / Clean Site
820fcd2f-22d1-43d9-9c3c-a01e9720d0f3 | checkpoint | Final clean and grade site area affected by the fuel gas services scope of works. Excess spoil removed in accordance with terms of the contract
325b0f8a-c05b-425e-8ebc-bee016626f8c | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
8ab7b795-9d75-4a90-95f1-d0c345d525d9 | section | Final Inspection / Completion
12992cf4-5ab3-412b-9c96-80644a358260 | checkpoint | Verify all inspections, complete records. All Authority approvals have been received with Supporting records from Services Subcontractors
efa8c84f-5d7a-4b91-8487-94400f952061 | section | Record Drawings
5fbfe9fe-de17-4cb1-86f1-a7d3bdc82117 | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
089c2645-968a-440a-a0c8-2f78cb4361d4 | checkpoint | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
6b9f0537-2442-4b45-8f1e-a5d6feae0c37 | checklist | ITP 003 Hydraulics – Hose Reels |  | ITP 003 Hydraulics – Hose Reels
3b55b081-0606-402d-995b-13aef7723e95 | section | Scope of work
4152e028-ee11-4847-aad8-f695132d86d2 | checkpoint | Check documents are current & for construction
266e4349-9a66-4aab-91ee-2fc7bdeeb5fb | section | Competency
dfcd5785-bb3a-4fba-9241-e5105e65bf2d | checkpoint | Trade Registration
ac7eed4a-00b1-43b0-8067-a45d811a539e | section | Set Out
f2164215-8b50-4010-a288-0680c31cd5b3 | checkpoint | Mark out hose reel locations as nominated on drawings in locations. Location to comply with AS2441 clause 10.
3dd9e726-290d-42ed-bc8b-694b1fbdc0ec | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
359e91ff-a3e5-4c44-a6d7-00e8063154e8 | section | Pipe Support
1222660c-76d4-4a45-8d0b-ebd237bf1b9f | checkpoint | Pipes to be supported as per AS 3500. Extra supports to be added to prevent pipe movement caused by water pressure effects
3108ec1e-a338-4d19-945d-ea87ad335c38 | section | Hose Reels & Valves
beb10422-ddaa-430f-ac05-80f5b2bc1c42 | checkpoint | Check hose reels & valves for water mark approval as per AS 1221. Selection as per clause 9 table 9
e1d872b6-9497-4562-baa8-75fd943e87ee | section | Piping
19e6356e-12df-4808-a750-42700ff418e4 | checkpoint | Thrust blocks installed as per detail
98d365d6-7cc7-5ace-bdc4-8a1f26a83898 | note | AS2419.1 & AS2442 clause 6.4
b386a77a-d98d-4863-8b33-26ce95d2cfaa | checkpoint | Protruding services have been adequately protected from future construction damage
7737dc89-fdd7-4a34-900d-e22f1c22cd1d | section | Marking & Labelling
1d86f1fe-2fd7-4683-815f-c1e231ae0e03 | checkpoint | Underground pipework to have identification tape installed.
962c6937-1cf3-4885-8e7c-ab9b3a87827a | checkpoint | All marking tape is in accordance with Australian standard
9fec334c-8619-4f3d-81eb-28a38865e59e | section | Pressure Testing
4d497f22-bdf9-44c9-aaf6-136ebdbfab16 | checkpoint | Prior to testing the system shall be flushed of all foreign matter.
3fbbdc13-9c30-46d0-b93a-b99b244902bc | checkpoint | Hydrostatic pressure test before backfilling, lagging & covering. Pipework with elastomeric or RRJ shall be backfilled leaving the joints exposed. Test as per AS 3500.4. 1500 KPA for 30 min. No leaks are acceptable. Some fixture cannot handle 1500 KPA.
47b13ddd-cdbd-47ca-a186-d2d3c194bac7 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
9e213f30-6c33-4ca2-a91c-9598b982f100 | section | Backfill Compaction
0b90da59-fcd0-4951-b21d-18c1d4047bce | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil
8175765c-af60-413c-87d3-2890c882c085 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
5193b402-5dd2-4246-b246-efef1fe69204 | section | Final Trim / Clean Site
4365a593-4a14-4f35-a24c-165274a7ee5d | checkpoint | Final clean and grade site area affected by the water services scope of works. Excess spoil removed in accordance with contract terms
e3dd02f0-2df1-4d78-b5ac-b315decab358 | section | Final Inspection / Commission
02654ad7-5596-4dfb-92c4-d180fc85c7e3 | checkpoint | Verify all inspections, complete records Hose Reels to be commissioned as per AS2441 clause 12.
67f405bd-733a-4a3c-a0f8-e2138f8e5c87 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
53d3d0d1-d1e4-43e7-8dd6-baa79b3deef4 | section | Record Drawings
90da4d6e-cbac-4546-a79c-19507f430fb5 | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
33258d06-d4a0-58b2-8050-01f9d0e4e54f | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
c1bf34d0-6944-467e-9fb2-11c2c834bfec | checklist | ITP 004 Hydraulics – Hydrants |  | ITP 004 Hydraulics – Hydrants
2810180b-fbcf-4b15-81c1-74b33d50fe8a | section | Scope of work
16fe67ee-c96f-434d-bc33-2fdd5c5fd6af | checkpoint | Check documents are current & for construction
ee124b41-6e3b-42b0-a26b-6095bd885ad1 | section | Competency
4b056c74-8a43-4d7c-94e9-75a907913536 | checkpoint | Trade Registration
120aaee8-a82d-4df5-af3c-b13dae4c2acf | section | Set Out & Service Location
965f1c5c-b812-4697-9411-8dc8d4eddc37 | checkpoint | Mark out hydrant locations as per contract documents and compliance with AS2419.1 Fire Hydrant Installations.
be0ebbc6-0dc3-4ec0-a4da-65c78bc2401b | checkpoint | Services in trenching area have been located or shown on documentations prior to commencing works.
aa7efb71-e54d-4637-855a-d64c776d6e8e | section | Trenching
3e68c2bc-021b-4290-905c-30e4876e5617 | checkpoint | Where excavations are >1.5m deep Services Subcontractors have prepared a Safe Work Method Statement and submitted to HY and permit completed
4c06e934-4c84-498e-902f-8ed32830d9ba | checkpoint | A Plant Safety Verification has been conducted for all mobile plant to be used for In Ground Services Installation
e8871230-d294-407a-b1e4-e073788cfdef | section | Pipes Support
68d00132-04e7-46bd-8966-61a6d0ea9772 | checkpoint | Pipes to be supported as per AS2419 clause 8.7. Vertical & Horizontal support as per AS2491.1 Fire Hydrant Installations. Table 8.7.7. DN80 Max spacing 5m, DN100 Max spacing 5m & >100 Max spacing 6m. underground pipework to be secured as per AS2419.1 clause 8.8
71f1fdb1-b645-47df-9cf7-66ab38ae6e32 | section | Valves
9e8249d5-fcf8-407d-a026-6eb05df49280 | checkpoint | Valve to comply with AS2638.1 Gate valves for waterworks purposes ,AS2638.2 Resilient seated gate valve & AS3579 Cast Iron Wedge gate valve for general purpose.
bfdd59cf-de0e-447a-bce7-a5ce35aeef30 | section | Piping
1b13dded-e6b5-4084-966b-4ed032d4adb9 | checkpoint | Pipework selection and sizes as per specifications and for construction drawings.
7cd05f3f-b62f-47dd-ab88-49cce7d23145 | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
21876fe7-df3e-46f7-a772-0e10c18c7956 | checkpoint | AS2419 Fire Hydrant Installations
c0722214-5b07-42a9-9414-80a918b47378 | section | Marking & Labelling
84608ba9-fa6b-4188-8599-fd2a2f1f204c | checkpoint | Underground pipework to have identification tape installed.
e4d29e6c-5b59-4e73-9a1f-d86d45351649 | checkpoint | All marking tape is in accordance with the Australian standard
2b40aa65-ea36-47e6-83fc-f18938173556 | section | Testing
0829e432-7074-4d5a-80d2-37de2333fb7a | checkpoint | Prior to test the system shall have all air and debris flushed from the system as per AS 2419.1 clause 10.2.1
2eac846e-17bb-466e-9ab3-38eea7fea0fd | checkpoint | Hydrostatic pressure test to AS2419.1 clause 8.4. Pressure tests at 1500 KPA or 1.5 times the design pressure whichever is the greater for duration of 2 hours. If pipe work is underground the test shall be made before covering of the joints takes place. The pipework sections will be partially backfilled for securing during test.
11694fcb-f99b-4f3b-b05c-e2c7d6eb1fac | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
9c5873a3-6851-4fa5-80c7-2083c2a684a1 | section | Backfill Compaction
84552f00-98c0-4e00-8a4a-065bdb3a60b2 | checkpoint | Photographs of installed services prior to backfill.
a1b984e8-5fca-4384-8503-2958c94b044d | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil
3ed42a5d-a935-4164-b801-c9f57d1f379a | checkpoint | Bedding material and trench backfill is in accordance with IFC Drawings, sample submission and specification
b893bcd3-693e-5663-9837-a130f67e83bf | note | (Bedding material grading certificate to be provided)
64989ec9-24d4-4eb5-acab-679ab510cd47 | section | Final Trim / Clean Site
14fe23c3-b45c-4125-8c2f-a7fb390d818f | checkpoint | Final clean and grade site area affected by the water services scope of works. Excess spoil removed in accordance with contract terms
93bfa7ba-845f-4d74-bc3b-6aa484d0c56d | checkpoint | Excess spoil removed in accordance with contract terms
bc6cc23c-b1d1-48ab-9777-090c0849a1e3 | section | Final Inspection / Commission
c5732e89-4769-4044-93a5-68adc76ab775 | checkpoint | System shall be commissioned as per AS2419.1 Fire Hydrant Installations clause 10.3. Details of commission attached to back of ITP.
4eb00421-0cca-4968-a0de-07337ca71ba2 | section | Record Drawings
8c1f48c9-ad24-49ed-9535-7f90db33c64f | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components. Provide verifications of testing
50c7694f-2a12-4d87-9e97-e55031683064 | checklist | ITP 005 Hydraulics – Hydraulic Pumps |  | ITP 005 Hydraulics – Hydraulic Pumps
e9a1ad37-b018-4a87-bf60-4f1924fccc3d | section | Scope of work
3a3068dd-3c1d-4e39-b81e-191da9366385 | checkpoint | Check documents are current & for construction
efc080e2-99ff-433c-90b6-cc16e4f67b50 | section | Competency
fca3888b-24c6-4be5-bf60-ae1ac4ffe3bc | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
1e21f98e-38f0-44ef-be99-d1c4097107c1 | section | Set Out
7df085d8-9214-418a-b8a2-ccff96aec4ae | checkpoint | Review current for construction drawing for pump locations.
ea6f293e-a3b4-4289-9ae5-5102cb06a69e | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
9f71a3f5-5b62-4c3b-af70-508591ff07dc | section | Pump Selection
e9bee9dd-69a1-483b-8618-75b3cb263082 | checkpoint | Specifications, design documentation and issued for construction drawings
9712f45a-4e34-4d8c-85d3-041f2efe4cfc | section | Testing & Commissioning
78e5ce99-d7bf-42a9-b152-b03c838f9c45 | checkpoint | Prior to testing the system shall be flushed of all foreign matter.
365a65d5-472c-432e-be76-7e06123dafe2 | checkpoint | Pumps shall be commissioned as per the manufacturer's recommendation.
61276108-a482-406c-a2be-423263942843 | checkpoint | Pump Operation – test for correct rotation
5ae4a065-c750-4328-9088-6b5904bfcbc4 | checkpoint | Automatic Changeover – Test changeover sequence under all operational combinations
3ea30438-eea9-495b-b4d3-bcb82c5e9eb6 | checkpoint | Level Controls – Operate pumps, measure levels and adjust if necessary.
c9ab0e79-38cf-426f-b91b-8136f7392b26 | checkpoint | Safety Controls – Simulate fault for each safety control
f3a2d3be-48d5-4a8d-a727-79a4b7f2b8d9 | checkpoint | Alarms – Simulate alarm condition. Verify correct alarm raised.
adeee6fd-83ed-40fc-a70c-d2e2eecc119c | checkpoint | Motor: Measure motor current and adjust overloads to suit.
1c8d4edd-9c9c-4394-933d-b4c3675c3409 | checkpoint | Completion test – Provide a full operational test to verify compliance.
2ef6aafb-b194-46b6-aaf2-b754c779e873 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractor.
7faa664b-05c9-4947-95ce-cbe0d48fe676 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
6c1b3353-e5d6-46ce-8ea1-b641b9f60637 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
809e0f61-5ddf-4780-b96e-f38969f3c914 | section | Record Drawings
0a2319fb-b8f1-420d-9c74-e63ca5f61c97 | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
a8c20f9a-2167-580e-b223-9864fe96c8e9 | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed
b7d58ff8-9502-4206-98e0-537d41223579 | checklist | ITP 007 Hydraulics – Stormwater |  | ITP 007 Hydraulics – Stormwater
a25ef2cb-d8c6-4312-ab7a-832eee4c712d | section | Scope of work
dec73b1e-fc19-4215-afc6-11b1db6e88a7 | checkpoint | Check documents are current & for construction
5c09bf2f-1974-4b5c-aea1-d7fa69e8c9fb | checkpoint | Check levels & falls
0cd09458-b5e9-49bf-9a55-85d492c0907b | section | Competency
bfa9c738-59b6-44a6-8876-2714677c8d35 | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
3d5a729b-5164-4071-9a6e-8c65dd5c29c2 | section | Set Out
24ee8b47-f02b-448c-a0c1-1793aeaa2b51 | checkpoint | Mark out pipe locations and co-ordinate with other trades.
0b70f4b2-8f40-410b-a597-f53c43c3d1a8 | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
ab20415d-a382-40af-a1de-561ff4dfdb46 | section | Pipe Support
b5752a06-cc3a-4356-9be9-f2e05365f45d | checkpoint | Pipes to be supported as per AS 3500.2 Table 9.1
33f90a25-19ce-45f1-ae77-c490b3138db9 | section | Pipe Laying
51dda6af-11f0-44cd-88ba-91924330b6a6 | checkpoint | Pipes to be laid in straight lines between changes of directions. Pipes are to be laid on base of crushed hard rock or coarse washed sand.
c3c71b8a-34d5-4259-9aa5-6fbd5f0b97f8 | checkpoint | Pipework selection and sizes as per specifications and for construction drawings and AS 3500
76242bcf-e39e-42e9-9bbc-376bf8b74e02 | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
e5fb6ef8-cb7c-4cbe-972c-9175ea85b584 | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
d3e30f8c-be00-4da3-9c3c-dc6a91d5d940 | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
04f9a460-1689-4e80-9db6-1cdaa2d314f8 | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
8b7846f8-90b6-4b70-aea1-55483607cfe3 | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
6891706a-1503-4271-90c9-9892ac42b18e | checkpoint | Penetrations are of suitable height and have been capped where required.
3ef2a669-343d-4fb1-bb8d-aaaccc0d30df | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
3b9309bd-9773-4c33-be5e-09fcc54cf8ab | checkpoint | Pipework have been installed without damage
187ea635-024b-483b-b5a0-e208bf35af28 | checkpoint | Pipework Joints have been appropriately treated/glued
f64c7cfd-388c-4d27-ad16-d60e0bac7db1 | checkpoint | Thrust blocks installed as per detail
91cb75a1-dcb7-43af-9662-73472e7ba3ec | checkpoint | Protruding services have been adequately protected from future construction damage
09c6de30-9f98-4a4e-9362-606474d1622a | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
0808abab-425e-458e-9e80-a424eb1d20db | section | Marking & Labelling
a4d05315-f0d0-4ab1-ba8c-b54a1ac014df | checkpoint | Underground pipework to have identification tape installed.
a75a1743-dafd-4b3a-88a4-98d36e2edea2 | checkpoint | All marking tape is in accordance with Australian Standards
f4afa5fb-dbf9-49d4-b7b8-a86a38b90574 | section | Pits
df2e37cd-a4b1-4c85-ad31-40739b79b1d8 | checkpoint | Pits to have smooth, seamless finish using steel trowel or concrete cast in steel frames. Design and for construction drawings
8019d621-3f0e-4a69-91a2-ed5e2ee1e847 | section | Testing
77167e5d-f807-47a7-bf95-6b672c303047 | checkpoint | Test to AS 3500.3 Section 10 Clauses 10.3 .1 & 10.3.2 Hydrostatic Water Test for a period of 3min.
f8ea57c5-02b4-48b0-9ae5-2af7598fd0fd | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
9a62eb0c-4247-4694-8005-905eeaa8af8a | checkpoint | Protruding services have been adequately protected from future construction damage
c1379fff-c304-42be-9be9-8ce2f0b9f3cb | checkpoint | Inground services have been inspected by the relevant authorities/consultants prior to closing up (witness/hold point)
f4755089-ecc4-466b-990f-db051cc5df46 | checkpoint | Pipe/conduit compliance record/certificate
c8a81276-412f-4b6e-bd1d-0acf9d927aac | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
b953658c-775b-44eb-8388-0314856c97d7 | section | Backfill Compaction
d51e3f03-4d27-4b84-9831-3e581e67122d | checkpoint | Pipes are to be laid on base of crushed hard rock or coarse washed sand. The balance of the trench to be filled and compacted with selected removed spoil.
98fe29d6-de6a-4aad-a1b3-154243064f2c | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification
585aeb2f-9cc4-490e-8823-5b46a5ce23f8 | checkpoint | Bedding material grading certificate to be provided
fbd0c3ba-a082-4bd0-94e4-18252d02fadc | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
f64064d5-d6a8-4617-92f9-e9f6ff7ae3d1 | checkpoint | Photographs of installed services prior to backfill
ed5dea94-1f96-4413-bf34-3b68a522b458 | checkpoint | Surfaces disturbed during services installation have been adequately reinstated/repaired
b049e413-bb6a-43b9-854a-f10dfaf126ab | section | Final Trim / Clean Site
62873cf6-7aa3-4f63-8cb6-2afee46e15ce | checkpoint | Final clean and grade site area affected by the Stormwater scope of works
a46273ac-5db0-495d-9a4f-4f44aed191cc | checkpoint | Excess spoil removed from site by as per contract terms
3d665016-ca86-4695-8a78-5394ed1f2fe9 | section | Final Inspection / Completion
e479784e-ee42-44c4-b598-bd5dab0dad1d | checkpoint | Verify all inspections, complete records clean and flush entire installation
a3dfd4d7-c8e1-4762-8f3e-2e33a7ba50d1 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
f9227ff0-3344-42d6-9035-75b2d30bbcab | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
e7826328-0054-4e90-9075-b9e55f1843d4 | section | Record Drawings
51cabe44-e1a0-451d-b234-cd8ba8d81492 | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
359d21e3-35ac-562b-b4a0-6113eb0e1739 | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
97fc6c2e-c6e4-4ea0-a079-55c5cdbfd0e2 | checklist | ITP 008 Hydraulics – Sanitary Fixtures & Tapware |  | ITP 008 Hydraulics – Sanitary Fixtures & Tapware
f3df8811-6ba6-4b27-95b9-a0b6ab45843f | section | Scope of work
ae3d7135-bbd4-45f1-98af-c820dc8ec922 | checkpoint | Check documents are current & for construction
366c47a7-7095-4daa-8dd3-767e4e9b437f | checkpoint | Check levels & falls
94392ecd-648c-45b4-afc7-41fabcd11ca5 | section | Competency
b5099e8a-78b2-4e5e-b67f-57f2ceda717b | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
606e50d6-44ad-464d-bc13-280adf9f1589 | section | Set Out
6a62c775-e614-42ae-a809-6dafc3b53f8a | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
d597acd7-df96-4a59-9a4c-e44ae20b6675 | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
42632392-1834-4c53-8bed-bc7b2d71d5fa | section | Fixture / Tapware Selection
9edfd134-09b9-42b6-8acc-2edb9f36c7eb | checkpoint | Refer to schedules in specifications and design documentation.
e121192c-df37-472e-8865-37893fb9deaf | section | Installation
05ab4e5a-9233-4c52-b77f-259d6eef90ba | checkpoint | Generally refer to manufacturer's literature for correct installation details. Ensure that items are installed level, plumb & true. Ensure that moving parts function freely and without obstruction.
260455ec-098b-42f5-8c96-73a7f924a151 | section | Testing
9965d9b6-5f3b-4699-9e52-c1fa5a699b89 | checkpoint | Prior to testing the system shall be flushed of all foreign matter. Remove all protective coatings, stickers and clean surfaces.
a6d0d923-2aa8-45c7-8ab1-097eb7b97058 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
b10d633d-8f82-4d33-bfa4-7c4468b8fb75 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
bfa22eb4-7408-468a-b177-902c3cec13a2 | section | Final Trim / Clean Site
c380e26d-1363-4af1-904a-069ff265a8bb | checkpoint | Final clean site area affected by the fixtures & tapware scope of works
4b02d191-1b37-45ca-ad7b-621347489178 | section | Final Inspection / Completion
37bb31c4-2ff4-4d5d-a6b2-02bf55b0c268 | checkpoint | Verify all inspections, complete records
fbf6b324-08ce-49e8-8a72-de71e9d6a585 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
955653f0-9598-47cb-ab88-30b75d5b808b | section | Record Drawings
582a8c66-ae0f-4f57-be47-187ab0d3f68a | checkpoint | Provide Requirement of contract including Dimensioned, Surveyed, Falls, Locations, Components
cee72f16-d854-5800-93b1-6f7d3da3852b | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
a0c02288-90f2-4563-b0a9-78f2f1c52513 | checklist | ITP 009 Hydraulics – Water Heaters |  | ITP 009 Hydraulics – Water Heaters
c965449c-d630-453f-a2eb-d993bfedeb55 | section | Scope of work
2026ddaa-2413-48d6-ab22-09029ae60f9a | checkpoint | Check documents are current & for construction
44fcc67a-1ac2-4a11-bafe-b6d32f1126d0 | checkpoint | Check levels & falls
fa06470a-8b0a-4d7d-b1be-32ebc48d58b1 | section | Competency
0d3306cc-5570-42a4-8a28-e2f5a1db4598 | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
da84d0f4-f87f-4ea7-b98e-c25165e6c265 | section | Set Out
bc431b34-fe3e-4290-9331-fb0b16f2c37a | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
efa12f8a-2808-45b4-89bb-f4159225582e | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
37339af0-35b9-40f5-adb3-b991f6786581 | section | Heater Selection
5715c518-5ed5-41c8-b0d5-abfff9d5bc25 | checkpoint | Specifications, design documentation and issued for construction drawings
daad55cd-2d73-4541-8d2e-2cf0f508a5a7 | section | Installation
a56a5946-3490-445e-9864-f1890fc1d786 | checkpoint | Generally refer to manufacturer's literature for correct installation details. Where applicable refer to AS5601 for gas appliance installation.
90a987cc-7b89-4552-9d2f-debab6e7b22d | section | Testing
21950369-459a-478b-a550-266a1ab4acb4 | checkpoint | Prior to testing the system shall be flushed of all foreign matter. Remove all protective coatings, stickers and clean surfaces. Where applicable test gas fired plant to AS5601 – Gas installations
ca068afd-bcea-4c4b-9713-1fcef21b4918 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
107a0f12-8186-4dd5-9fdc-79f4d1b13581 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
21c5a50c-3168-4b99-84d5-5972062cd3b5 | section | Final Trim / Clean Site
bea3ee8c-0067-44ca-a2d7-130089c93290 | checkpoint | Final clean site area affected by the Water Heaters scope of works
85a8f198-382a-485a-8f25-fa6c5f871741 | section | Final Inspection / Completion
c1d1a637-bf93-4171-9e0a-8a46e87f24f0 | checkpoint | Verify all inspections, complete records
d3bb774d-39d6-4ba2-b35c-072487bf64e9 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
705c3286-a80f-4268-8b76-4999697a8545 | section | Record Drawings
cfaa4e73-6300-456a-bb91-6e964ac795c6 | checkpoint | Provide Requirement of contract including Dimensioned, Surveyed, Falls, Locations, Components
321b5b26-9389-5772-98a4-7211b5e2d80b | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
991736c9-d9f1-4fd8-aafa-8691277c756b | checklist | ITP 013 Hydraulics – Inground Sewer Drainage |  | ITP 013 Hydraulics – Inground Sewer Drainage
62cbea20-92c7-4846-b449-815636f9c6f7 | section | Scope of work
11d15e37-9a37-453d-a2c2-767b17fd09dd | checkpoint | Check documents are current & for construction
909c2aa6-47b1-4197-9204-3096f807a2e8 | checkpoint | Check levels & falls
529cbf4c-5070-49fd-a316-af57c47dda4c | section | Competency
ca698228-663f-49bb-9be6-996c08cb9bd0 | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
f0f36866-a51b-4397-8411-f7ad765a7d59 | section | Set Out
0802f682-5217-4994-b86a-8c02104cae03 | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
1a83a6ce-cca7-464c-8d50-ce3a34d25575 | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
fbb0a8b3-cdb6-4721-a991-942ab2318d7b | section | Excavation
029e6cd0-c569-4b30-8e47-b90000d10e1a | checkpoint | Excavate trenches to minimal size
1a6a303c-368f-4022-a1e4-6c795d541042 | checkpoint | Grade Trenches to Falls
048f96a7-1be2-47b2-be18-0979f17367a2 | checkpoint | Bed pipes on 10mm – blue metal
1a4d6e2a-762e-4e95-b90d-ab4f84a23c2b | checkpoint | Surfaces disturbed during services installation have been adequately reinstated/repaired
d42ea91a-3b5c-4c0e-9c17-ec0b01a5d1c6 | section | Pipework
ecf4d715-de36-4cae-8ff9-187deb7d09de | checkpoint | Pipework is in accordance with IFC drawings, sample submission and specification
83f1d102-17e5-4c0d-a630-dd6ff49a60df | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
26657305-c029-4d84-b45d-64497d96723b | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
19e679f7-b8c7-476a-b686-20195a237dbc | checkpoint | Minimum separation of underground services is achieved
0ae7a6ce-4aa6-4b27-803d-0ab3ad4c4433 | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
4b1b9ae1-5a77-450c-bb73-7facdb8ef768 | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
3e2824d8-1904-4e55-b74b-d9b87ef4111c | checkpoint | Penetrations are of suitable height and have been capped where required.
d40303ba-5cb0-4552-b4d3-bbfe6c7c2b57 | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
71c53005-274e-4dcb-b336-13628846b023 | checkpoint | Pipework have been installed without damage
8b48239a-6055-4e35-a774-7cffe6bc1515 | checkpoint | Pipework Joints have been appropriately treated/glued
bfa5a920-0905-4c4a-8852-633c6e011e53 | checkpoint | Pipe/conduit compliance record/certificate as per specification
14215295-6b7a-4d2d-ba0a-8a61e8c8a302 | checkpoint | Thrust blocks installed as per detail
6d94d113-5975-422c-bf9a-cb0092ae0cb2 | checkpoint | Protruding services have been adequately protected from future construction damage
d27212fe-74bf-401d-96a1-500664da2ab8 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
bb948bbe-8f05-409b-823f-abfec7d4c250 | section | Pits
f1a60dee-bd58-4e16-bd6f-048d1b9234fe | checkpoint | Adequate Protection
f50ec1f2-b642-4dff-9bd9-72cb6277fca2 | checkpoint | Installation as per specification
4cf04df2-20a9-4b19-bcdb-10d2ea4d8fde | section | Backfill Compaction
1d855f06-1c5b-4737-b0ec-d7d49f7c6594 | checkpoint | Inground services have been inspected by the relevant authorities/consultants prior to closing up (witness/hold point)
d17dda21-ce1a-4fa9-99a3-c5bed29b7a2c | checkpoint | Photographs of installed services prior to backfill
57485f6a-de17-4e4a-97fc-012051b9fe5f | checkpoint | Backfill pipe with 10mm blue metal then backfill with selected excavated material
2758ff14-0473-4405-9a81-47fee47a4266 | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification.
e1a5ab3d-0e8e-4714-8e23-0c151059090d | checkpoint | Bedding material grading certificate to be provided
0c8a90ae-a122-4e4c-a5be-5166bd096017 | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
f4fa057e-4381-46a7-a3fc-62bd5f5c21ff | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
437cb4b0-be37-49f9-8f51-024f2b73810d | section | Final Trim / Clean Site
375d3e22-8fde-433b-a325-82b7e57fe700 | checkpoint | Final clean and grade site area affected by the Stormwater scope of works
09da2c89-a24c-4e7a-a7c5-b2bb240dea7f | checkpoint | Excess Spoil removed from site by others
9e73a1c5-0754-4dc1-9203-cbe085ef184b | section | Final Inspection / Completion
f87a6602-6bd9-4b63-aeef-ca34efa7b8a7 | checkpoint | Verify all inspections, complete records clean and flush entire installation
3e83c062-f728-42b7-bcff-82eb4edb61a0 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
4247db6e-fa20-40c7-b529-cf390d793144 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
558b8465-3183-4b83-b18e-9e90706807a0 | section | Record Drawings
95a3e7f8-1fb5-4764-ae15-5a3dc971213c | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
f99cec24-1814-563d-963c-bbb2a4215f5e | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
9dacc075-84d4-4779-bb12-2cdd51bc29bc | checklist | ITP 014 Hydraulics – Sanitary Plumbing |  | ITP 014 Hydraulics – Sanitary Plumbing
d36dd85d-fc13-49bb-93ad-c2f2e86c2b21 | section | Scope of work
1e21e261-0c22-41f6-b0ff-4f1b0bf5cf2c | checkpoint | Check documents are current & for construction
1eca8786-72c2-4523-ab34-5b8e2110c7ab | checkpoint | Check levels & falls
3cfcd83b-2333-4d5e-a886-3fdbbdadc3e0 | section | Competency
ed4d4c36-9745-44a3-989e-1683f15f9d54 | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
42c88dd5-b8ea-43ed-bc6d-fc47de469f0e | section | Set Out
54b2002f-8521-410c-80c3-b3c9e7f40ccb | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
09cf538c-9463-48f6-90d2-48c157cb2e69 | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
4d00294e-0fb0-4cc2-b744-1eaca08eab79 | section | Pipe Support
b1208ea3-a3d9-479a-b22f-f153fca1b67f | checkpoint | Pipes to be supported as per AS 3500.2 Table 9.1
31140de6-86cc-4e1b-8811-d9923105f9bf | section | Pipe Installation
d246cf1b-22fc-471b-91e9-66e9fd988fb7 | checkpoint | Pipes to be installed in straight lines, vertically and horizontally, between changes of directions.
e5025690-6b18-4e86-8d6e-1d401ea06c53 | section | Piping
676d7fb8-b4ab-4607-b6a9-dccf8abb5ed4 | checkpoint | Pipe selection as per Specifications. Pipework sizes as per for construction drawings.
65637801-1b08-4afc-ade9-020b97a7f09d | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
1182ece5-3295-49d6-a335-1b76cb344c1f | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
86947a91-7ddd-4b10-9ed6-51fa07117e05 | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
e62d118d-6a2a-44ad-a1c4-60989fbf0b57 | checkpoint | Penetrations are of suitable height and have been capped where required.
b3925c09-706d-44b6-980a-e2b04c4214b9 | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
a70b3430-e0b6-48c5-b051-84520ad4c623 | checkpoint | Pipework have been installed without damage
94a6c2c3-548f-4830-8e6e-beab5a374827 | checkpoint | Pipework Joints have been appropriately treated/glued
e570c767-974d-4bc3-af4a-057ad630c1eb | checkpoint | Pipe/conduit compliance record/certificate
aec05b90-87a4-4e2e-95d2-828523fa61eb | checkpoint | Thrust blocks installed as per detail
1613cb15-5d55-49e5-a7c8-6d8aaa0b5233 | checkpoint | Protruding services have been adequately protected from future construction damage
2bcf824f-57ca-4460-87a5-2f6ba7b159c4 | checkpoint | Pipes to be labelled as per Specifications and AS 3500
eed52cf6-451d-4f71-81fc-0c300808c320 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
404f3fb0-e08b-4517-996a-100f516cf2b6 | section | Marking & Labelling
6f33cb02-b18c-4930-a62e-3941f55421af | checkpoint | All marking tape is in accordance with the IFC drawings, sample submission and specification
397bb4c3-3e04-4377-94c2-302949e87010 | section | Sewer Access Chambers
e0f833c4-ab1b-451c-93f7-297c096cbe90 | checkpoint | Chambers to be installed as per Specifications.
40ffb954-c85f-4af1-83a7-7067ce6b1e30 | section | Testing
6f2f023e-c055-418a-9e6c-1e861edfb119 | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
50b86e46-dc57-4dec-b75a-320ee10b34f1 | checkpoint | Test to AS 3500.2 Section 13 Clauses 13.2 & 13.3 Hydrostatic Water Test
212ff9ff-413b-4869-a02e-d84bc0ce15af | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
a5d590ec-181d-4a14-80d2-39cc9c21a0ad | checkpoint | Verify all inspections, complete records clean and flush entire installation
5cdfb6dd-d1b1-4f25-8302-1d015075b7a3 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
20316de7-a59c-4f62-8ba1-01125e20b523 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
7f6b5a11-73ad-4f0e-9426-912229c836c6 | section | Final Inspection / Completion
8050bc59-375e-4be1-b310-6fb3f46a2d24 | checkpoint | Verify all inspections, complete records clean and flush entire installation
fd39d303-6b93-4147-a197-277717d64a9d | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
a1e8b10a-f91c-4f11-8823-f3d973088841 | section | Record Drawings
2f10deb0-a145-47b9-8d88-81e1babdc668 | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
d7daca1c-8b63-57a1-a78b-592fb68674eb | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
d93048a5-ae2e-4354-aa54-48a9cda105dd | checklist | ITP 015 Hydraulics - Commissioning of Plant and Equipment |  | ITP 015 Hydraulics - Commissioning of Plant and Equipment
68ee2d6d-9e53-4055-8140-cd3b5e35d090 | section | Scope of Work
5e3f4e77-ba9c-4d2f-b3f7-e1ecc76f95ee | checkpoint | Check documents are current & for construction
3b41436a-fa86-42d7-a566-402f5233515c | checkpoint | Location of all plant and equipment will be in accordance with for construction drawings and documentation
c05a4e33-c7eb-54d8-a517-b15c1a5837e9 | note | Plant and equipment will be in accordance with the Hydraulic Services Specifications
802d677c-1605-5166-a868-cba29316a8e3 | note | Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
d4df24ac-cac7-414d-a5e5-78bc62523587 | section | Competency
eeaeb2d8-20cd-4d0b-a847-eca83064fe2f | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
3b14403e-f0b4-4866-94e9-8e7ec4ccb70c | section | Set Out
ebf5e3c0-1f46-44d3-b60f-55727d7d5ce7 | checkpoint | Plant and equipment locations will be determined using dimensions on construction drawings and will be coordinated with all other associated trades
0a91c65d-93c4-4fd3-9dc6-7f27695442ee | checkpoint | Manufacturer's details for all plant, equipment, water meters etc will be referenced during all set out procedures
1e1a985d-23e1-4019-8c77-3d4deceeacc1 | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
9799fe47-91d0-4a99-87e0-863ffe625483 | section | Pipe Supports
46cdbb85-c2d7-4b93-b4a8-a388c2084918 | checkpoint | Pipework will be supported in accordance with AS 3500 and the Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
995e1cba-7d52-48f4-9881-841a9e0b6f67 | section | Valves
d312098e-5659-4ab4-b9f0-c46f22d6afcd | checkpoint | Valves will meet the requirements of the Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
8bc0e5d0-ce73-55e2-b2ae-4b307112a95e | note | A detailed valve schedule will be provided for easy identification and purpose
36970652-b9ca-4a93-ac8a-74005d29853c | section | Piping
caec3f1b-7e56-4a5c-9eaa-da9c9e7678bb | checkpoint | Pipe selection and Pipework sizes as per AS 3500 and Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009, sample submission and IFC Drawings.
816475f7-e832-466d-913c-04c4cbe5806d | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
2d966354-e7e0-455a-b8fc-a0e633bd92f6 | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
af8cf2af-1095-42a7-a4b0-f293dc30b205 | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
6ddbb146-856c-430e-a82e-aa1a50f5c08b | checkpoint | Penetrations are of suitable height and have been capped where required.
4f9ab1c4-a798-41c6-9f94-a1034d76fafa | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
c21513a0-e68c-4d44-a027-46aa44e3e5d4 | checkpoint | Pipework have been installed without damage
81e7c0e1-425d-4485-9ff7-d380ef2c8627 | checkpoint | Pipework Joints have been appropriately treated/glued
e821f969-7b56-4dc5-a7de-a4fdbf5f62a2 | checkpoint | Pipe/conduit compliance record/certificate
bbf960ce-47dc-4388-a9e9-552f96dcdec3 | checkpoint | Thrust blocks installed as per detail
b9239423-6eaf-47ba-b99e-c85e047a28a1 | checkpoint | Protruding services have been adequately protected from future construction damage
226e3298-05e6-41d1-a552-69dcb1e4fa73 | section | Marking & Labelling
f1183b53-dd00-4d21-9c70-9407c50be2e2 | checkpoint | In accordance with AS 3500.1 and Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
16078ef3-d1df-4cf7-b37c-4f8b4c856834 | checkpoint | All marking tape is in accordance with Australian standard.
8e96f18c-ff2d-40d8-a95d-73734946c3ba | section | Valve & Pump Pits or Boex
3e4a5390-6ced-4fc8-bb2b-45fdc8ee5180 | checkpoint | In accordance with AS 3500.1 and Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
72a1d2f2-de2f-4299-a0f2-0a0efa686da8 | section | Testing
09763b25-7438-46b4-b552-754493c3bf97 | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
cefd41d5-5556-45fe-a43a-c7eed609ced5 | checkpoint | A register of all testing equipment and calibration certificates will be provided prior to any testing and commissioning procedures commencing
d0e895b7-3ca0-4e18-9804-f8d7358b1de5 | section | Clean Site
5c8be616-2978-4f7c-9899-689637eeebeb | checkpoint | Final clean of the site area affected by the scope of works
564b9efb-62ac-4d21-a45f-2a1905473ad8 | checkpoint | Trade waste and excess materials are to be removed from the site area
d5167ab0-c25b-4e98-8ced-93d0bd94321d | section | Final Inspection / Completion
d6519bd5-8f25-499f-b928-9eb07ab27e42 | checkpoint | Verify all inspections and complete records
3e1d8b50-83e8-40ac-9769-0bd7b4d98764 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
94186bfd-6e59-484d-a791-9acb8da92340 | section | Record Drawings
2b248396-aef5-4f06-9acc-2f38afaab755 | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
f7d31ef5-eb9a-52f8-b789-9bdf487b813f | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
5dadf4ea-bd3b-429d-ac3b-2a5a297ae684 | checklist | ITP 016 Hydraulics – Trade Waste Drainage |  | ITP 016 Hydraulics – Trade Waste Drainage
11b729b6-ce4f-452b-9cd5-3807c9e79179 | section | Scope of work
8af553a1-fe99-4878-bca6-7cb9896e0bd0 | checkpoint | Check documents are current & for construction
7ad2e711-56ce-4dfb-8b85-635be364b429 | checkpoint | Check levels & falls
0f068c22-2fcc-4212-993e-bd310564cf45 | section | Competency
9ac032ee-0f49-4ed6-b025-82b6f5c83c6f | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
96975646-250a-4d2c-82d0-443197dad73b | section | Set Out
a19ca39a-ddb0-41ff-80ba-75eeaefc420b | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
65ab860c-0d9e-42dd-9587-384620c9643e | section | Pipe Supports
c1f0d314-0cb8-4b09-8360-98823c71a15a | checkpoint | Pipes to be supported as per AS 3500.2 Table 9.1
480e4a77-f338-4bd3-a2d8-e172d060e387 | section | Pipe Laying
b9ff8083-eaa2-4ac4-b7e5-b2e14e25addc | checkpoint | Pipes to be laid in straight lines between changes of directions. Crushed rock, gravel screenings or recycled crushed concrete, roof tiles or bricks of nominal size 7-10mm. refer to AS 3500.2 Section 5 Figure 5.1 for bedding section detail. Pipes to be laid in straight lines between changes of directions.
6a077f46-0f98-4534-8e4f-a45784d6cc16 | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
89d3f8cf-4aa2-4234-a752-1800687b8ede | checkpoint | Thrust blocks installed as per detail
9bb5790f-f77f-4c14-83f4-41f726568f04 | checkpoint | Protruding services have been adequately protected from future construction damage
7f5a2753-b9dc-4e62-b330-7f5cdc706843 | section | Piping
4e934bc6-7c58-4bc9-978f-8329d031ce96 | checkpoint | Pipe selection as per Table 4.1. Pipework selection and sizes as per specifications and for construction drawings. Pipework is in accordance with the IFC drawings, sample submission and specification
cdffbc84-3a39-467b-93e4-ea7a3e2e8ffc | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
f6c259a5-971c-4096-8ae2-504b38df096e | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
283ca312-28d9-4845-a07d-1712a31bff06 | checkpoint | Penetrations are of suitable height and have been capped where required.
2af0aeb3-39e9-41fb-a312-11f64c520dfc | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
d1c983f2-f411-49cf-a3d8-0a30aae99631 | checkpoint | Pipework have been installed without damage
eb45afc6-2db9-489a-ac56-79b4bd06e6c9 | checkpoint | Pipework Joints have been appropriately treated/glued Pipe/conduit compliance record/certificate
3a561ddb-2681-4980-b7e5-9f2ea3b539ce | section | Grease Arrestor
d553aa0d-e68c-41e6-9b0d-d2bf0b04d144 | checkpoint | Location and depth as per specifications and for construction drawings.
85d88839-0a1b-4173-b7f6-ac4b5b9cb774 | checkpoint | Installation as per Manufacturer's Guidelines
c6c091d1-b64f-465f-9756-8b814d67b46c | section | Testing
c8e5af96-0fcc-4c14-b52d-a05ea4f02be2 | checkpoint | Test to AS 3500.2 Section 13 Clauses 13.2 & 13.3 Hydrostatic Water Test or Air test to 30 KPA for a period of 3min.
488304bb-e20e-4c14-9b7f-d00d47212c02 | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
40e81a41-ef5a-46c2-a933-4351c1cb5035 | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
891bdcb8-a6c3-432c-af0c-f64da9fb7186 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
05c0a021-0515-44e6-a785-82b3e71a8f4e | section | Backfill Compaction
2c95fd62-2735-4415-8dee-2a8cdcb5eea9 | checkpoint | Backfill pipe with Crushed rock, gravel screenings or recycled crushed concrete, roof tiles or bricks of nominal size 7-10mm and fill balance of trench with selected excavated spoil and compact to standards.
7f8f4635-3db7-4248-9ea8-43862c64ed4e | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification
34d7b9f0-a33a-4c41-8c83-35814f282b7e | checkpoint | Bedding material grading certificate to be provided
c0a11cb5-8cd7-4385-b677-645ca2a223bd | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
d168aaa3-f5bc-4b85-bdbd-7d563f669314 | checkpoint | Photographs of installed services prior to backfill
e1d88728-f175-445d-939d-0eee4eff2052 | section | Final Trim / Clean Site
3424f0bf-2bf6-4519-89c0-ad6f6a4204e3 | checkpoint | Final clean and grade site area affected by the wastewater scope of works. Excess spoil removed from site as per contract terms
9228508e-5474-4460-af3d-44c721b61f4f | checkpoint | Verify all inspections, complete records clean and flush entire installation
118f1cd5-bfc4-43b2-9e81-0373ce8c6b73 | section | Record Drawings
93805f2e-a4d8-4194-a8d5-f2316b6d4b3f | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
66c02ad2-e2cf-5492-8c51-4335580ec766 | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed
8916c1ef-ad64-42d4-82c3-c95cfc7e7f26 | checklist | ITP 017 Hydraulics – Penetrations and Core Holes |  | ITP 017 Hydraulics – Penetrations and Core Holes
d52dae02-02c0-439c-a919-a9b490f32537 | section | Scope of Work
886d6ba6-2237-464d-bd08-f10fb77c5930 | checkpoint | Check documents are current & for construction
366b81f3-8ac8-586b-9f75-4158b8b25ca0 | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
58417c41-432b-4555-a35d-2250ddb3d3f9 | section | Competency
42be3585-2c69-4110-8e7e-d94ceaba8cd4 | checkpoint | Trade Registration
3f3292ae-4921-40e4-bcf1-fd6f8c9ca67f | section | Set Out
714b664a-e487-4806-8fb4-598390e39e95 | checkpoint | Mark out Deck. Check Hydraulic Shop Penetration Drawing is current.
94fd827b-140a-4275-95b7-0e5fdbc95b0e | checkpoint | Correct height of sleeves and or Fire collars
ae873be2-cb2f-4ec1-83d7-5dd34f54494b | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
45551af3-54e1-4145-a8d9-11a792b08ddc | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
0cc693e3-de76-4784-a28d-a0670dad1f70 | section | Material
55f01793-a060-4b8c-a8a3-d2ca96c91f38 | checkpoint | Confirm fire collars are approved for the relevant materials being used.
71f025a2-96bd-4148-9af4-d89cbaaee883 | section | Location
a2ede3dd-7229-4156-bde7-843eae9bbcd4 | checkpoint | AFC Hydraulic Penetration Drawings used
6201d9db-0513-46d4-bb01-238d0d77a19d | section | Check
08ed1300-92f9-411b-acc9-8fb43640d340 | checkpoint | Visually Check penetration are all in place against Drawing none have been damaged or removed by other trades
0253d7cc-b647-4e8a-9db0-dccd2d4d746d | checkpoint | Penetrations are of suitable height and have been capped where required.
9c5a9746-abb2-4905-9f3e-e1b94c6d0e61 | checkpoint | All Authority approvals have been received with
a2d79937-94f3-42d9-aead-1b5ff1aebd34 | section | Prior to Pour
22753879-d798-4746-9a15-ad30706a414d | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
4753a0af-2826-476d-bbfe-4fca7baeccbd | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
7c6d5056-593d-41a0-a1c7-a54496f72da6 | section | Pour
790bcba0-95f0-4f4b-81a9-7f39486b33db | checkpoint | Person present duration of pour
ac5f4e0b-e528-4277-9a44-a4b21961b757 | checklist | ITP 018 Rough Ins (Cold, Hot, Warm & Recycled Water and Gas) |  | ITP 018 Rough Ins (Cold, Hot, Warm & Recycled Water and Gas)
c2d9ff4f-e1bb-4d00-acdc-dde0324814a8 | section | Scope of work
6d85bc20-29c3-4043-8d77-28d66155b8cb | checkpoint | Check documents are current & for construction
e18a8156-b78c-4107-b946-577616189ad0 | checkpoint | Check levels & falls
94600efb-b90a-4f20-92e1-d296a429e077 | section | Competency
1322fed2-d5db-405c-af18-b07ac1f309e8 | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
fe6afacd-c035-4a21-a6b4-c5dcfd6a888a | section | Set Out
01222ef7-3cfc-42c2-9700-00ef4b55f34c | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures
f6a0dda1-8d37-4ad7-84ef-a6034c62b87b | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
7aa6f482-6565-4cd9-84e1-80882e97759f | section | Valves
f01d0d70-5470-4890-b421-8c0d49191b82 | checkpoint | Check valves for water mark approval.
feba873e-eb61-4cd3-97ff-e953d5a9525b | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures
bb5eed41-5e71-45c3-9a1a-8dbf2f55bf8c | section | Piping
c3d7dc08-727a-44b4-b3ee-bb4c1ac6e70f | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures
761f5bd6-eddb-40c3-aab0-b9bc6965debc | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
80632013-e642-416c-9dc7-e14867eb1245 | section | Pipe Installation
81f1dfc2-52d5-43b5-92cf-6c509292fb65 | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures and no damage to pipework
d2c3ae06-0de1-4744-bcd2-4e29d8eaf6ce | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
46231e6a-eb1a-4a28-868b-86623abc4adf | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
a250096b-ec17-4018-a7c6-833c78014e27 | checkpoint | Penetrations are of suitable height and have been capped where required.
aeece757-2858-4630-b158-17445d88c90f | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements Pipework Joints have been appropriately treated/glued and Pipe/conduit compliance record/certificate
c34a59d6-849e-469f-a326-a18483055ece | checkpoint | Thrust blocks installed as per detail
ce2a2854-2957-40f6-90b1-00446c29b076 | checkpoint | Protruding services have been adequately protected from future construction damage
f6549bc5-a61d-419c-bf71-46ce47aa14ab | section | Marking & Labelling
cc91f0a6-95a2-4148-a69c-3b99bd89714a | checkpoint | Pipework to have identification stickers applied as per AS 3500.
d543e760-7972-4063-8994-1c31557f5a54 | checkpoint | All marking tape is in accordance with Australian standard
d2f5ab17-2bb0-44fc-9951-feed693242d1 | section | Testing
e0ae70f9-b4b3-4be6-88a4-1f7dba70c60b | checkpoint | Prior to testing the system shall be flushed of all foreign matter.
cb4255a2-21e6-4656-a9c1-2e315605b51a | checkpoint | Hydrostatic pressure test before wall and ceiling sheeting is commenced and where applicable as per Infrastructure Authority requirements including applications, approvals and testing procedures.
0bb7c14f-5bba-4846-88b7-f2702a28c8c0 | checkpoint | As per AS 3500 or as specified
f569958a-9b4a-4ee6-b33f-a17039889ebc | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
01cc2041-0fd7-4eba-b9fd-91a5cf0e613f | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
1817d39f-5cff-4522-8859-d6dfa2aaa280 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
4d7a07cd-9fd8-45ef-a3c0-911e2f77ebf1 | section | Final Inspection / Completion
1f51b32e-d966-44a1-8d1a-dae74d77f652 | checkpoint | Verify all inspections, complete records
0100e1b5-0bac-475b-9e38-dc4129cc4907 | section | Record Drawings
35da6c05-5220-497e-929f-45b83bdbe0ba | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
325c5974-0c41-58df-bae4-0e1a9f66406f | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
211d1e8e-23ba-4cb1-9c19-f2e544c0465c | checklist | ITP 019 Hydraulics – Inground & Above Ground Sewer Rising Main Pipework |  | ITP 019 Hydraulics – Inground & Above Ground Sewer Rising Main Pipework
a2468e79-a24a-487b-b835-4e2cd000713f | section | Scope of work
e04e9b67-257b-4ed5-bc01-7a2612842a54 | checkpoint | Check documents are current & for construction
0c610156-6deb-4173-b78a-3f4ab6ffdb40 | checkpoint | Check levels & falls
ee5e7863-58ee-446e-8c5a-7cee15ff838f | section | Competency
58278a66-7307-47e2-a319-f1053985faeb | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
d600c0f2-d681-4740-b58d-11c0bbd8eafa | section | Set Out
c63bc79c-222b-4496-9083-db2d97dd2de8 | checkpoint | Mark out pipe locations and co-ordinate with other trades
673ed7fe-9539-4e84-8994-9c075ccde3a5 | section | Excavations
48cb0418-695f-4c07-a221-575aed840708 | checkpoint | Excavate trenches to minimal size
365d2d0d-7cde-527f-96f7-be978cfcbd10 | note | Bed pipes on 10mm – blue metal or Sand
c08bfa38-8aea-486a-a649-de6efad2f6a2 | section | Pipework Above Ground
a92d35da-a0fd-4644-9c5b-6b812ed34afa | checkpoint | Pipework installed on Bracketing with correct spacing between clips.
2abb094d-94ac-43a9-9626-2246e7a511ea | section | Pipework
2e241a80-adb5-46b8-8d75-9f4281d14469 | checkpoint | UPVC Pressure Pipework / MDPE Pipework
7aa00900-a200-436e-bfe1-dc4c31dd797f | checkpoint | Jointing methods as per specification
4fde3f38-16f6-4c6f-9f8d-f930520fcaa2 | section | Pipework Testing
083d133a-7bc8-4c30-b95b-108a5673176e | checkpoint | Pressure UPVC and MDPE pipework to be tested to 300 kPa for a min 30 mins.
03f4aa26-751b-4b54-b47f-1f5022a18883 | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
c88bc4be-34b1-4676-abc2-9f78f4e3eca0 | section | Sewer Connection
ed7bff6d-f7a4-4890-8932-2e750c78713c | checkpoint | Connection permit received
15177df3-3fbe-4410-8bf5-25b50124eb80 | checkpoint | Authority procedures followed
8b0f6067-dffb-43d7-b2e9-67220ce4173c | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
ae03d890-4c2f-4d83-8f96-24ab7f3f4b43 | section | Backfill Compaction
26677f53-992d-4269-b0c0-4afde202a22c | checkpoint | Backfill pipe with 10mm blue metal then backfill with selected excavated material
c2a8d720-65aa-4c11-a54c-b262959be642 | section | Final Trim / Clean Site
ca87650c-89ea-4f50-b963-83fd98ead95d | checkpoint | Final clean and grade site area affected by the stormwater scope of works
25faf709-4b9d-4185-981a-9b580344216a | checkpoint | Excess Spoil removed from site by others
7f505f0f-1c3e-4023-9e5a-1c1b4a8f6c85 | section | Final Inspection / Completion
a033887e-3d2c-4da5-b53e-655fd8fff52d | checkpoint | Verify all inspections, complete records