## ITP
|  |  | Inspection and Test Plan - Electrical and Communications Conduit Installation | [7 empty] | Document # DOT-31608-FUL-QAC-ITP-015
[11 empty] | Revision : 00 | 2025-05-05
Client: | Department of Transport & Planning |  | Construction Process: | Electrical and Communications Conduit Installation |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: | Melton Hwy/Leakes Road Upgrade |  |  |  |  | Name: | Mustafa Kamel | Name: | Greg Grima |  | Name: | Greg Grima
Contract No: | DOT31608 |  | Specifications: VR 706, VR 733 |  |  | Site Engineer |  | Utilities Coordinator |  |  | Quality Engineer
|  |  | Structure / Component: | Utilities/Civil
|  |  | Location: |  |  | Date : 5/5/25 |  | Date : 5/5/25 |  |  | Date : 5/5/25
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Test |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | Fulton Hogan | Other | Date
1 | Preliminaries / Pre- commencement activities
1.1 | IFC / Shop Drawings Submission & Approval. |  | Prior to Commencing | IFC Construction Drawings & Most Current Revision. | IFC Drawings | Document review | IFC Dwgs | HP* | Project Engineer | N/A |  | N/A
1.2 | Survey Set-Out |  | Where Required | Qualified Surveyor to set out extent of works on ground | IFC Drawings | Survey | Survey Calibration Certificates | WP | Foreman | N/A |  | N/A
1.3 | Excavation Permit/ Service Location |  | Prior to Commencing | Identify underground services NDD/hand dig as necessary. DYBD documents | Dial Before You Dig | Survey | Excavation Permit | HP* | Foreman | N/A |  | N/A
2 | Materials
2.1 | Conduit Sizing |  | Prior to Commencing | Conduit sizing to comply with VR table 733.021 Excludes utility providers designs and requirements | VR SS Table 733.021 | Site Inspection | This Checklist | IP | Foreman | N/A |  | N/A
2.2 | Material Backfill |  | Prior to Commencing | Unless otherwise specified, materials used for bedding and backfilling shall be uniform in composition and free from perishable matter and shall comply with the requirements specified in Table 706.061. | VRSS 706.03 | Site Inspection | This Checklist | IP | Foreman | N/A |  | N/A
3 | Excavation
3.1 | Entry/ Exit Points |  | Prior to Excavation | Entry/Exit points to be established |  | Review | This ITP | HP* | Project Engineer | N/A |  | N/A
3.2 | Minimum Cover |  | Ongoing | Minimum conduit cover shall apply as per table 733.031 Under Freeway Pavement – 1200mm Under Arterial Road Pavement – 1200mm Under Local Road Pavement –600mm-800mm Under Open Drains – 750mm Under footpath or unpaved areas (LV Circuits only) – 600mm Under footpath or unpaved areas (Extra LV or Comms conduits only) – 300mm | VR SS 733.031 Refer Individual asset owners specifications | Survey | AS Builts | SCP | Project Engineer | N/A |  | N/A
3.3 | Backfilling |  | Prior to backfilling conduits | Once the bedding material has been laid and the conduits put in place, works shall not proceed prior to inspection by superintendent or representative. For Vicroads assets only. Not applicable to Utility providers | VR 733.06 | Inspection | This ITP | HP | Superintendent or Representative |  |  | N/A
3.4 | Compaction Requirements |  | During excavation | Under Paved Areas - 98% Modified Compaction Unless otherwise specified, pavement material shall have during compaction a uniform moisture content within the range 85% to 115% of the optimum moisture content as determined in the Modified compactive effort. Bedding and Backfill (except pavement) Backfilling beneath areas to be paved shall be assessed for compaction in lots as defined in Section 173. The number of tests per lot shall be three. Backfill, the whole of which passes the 37.5 mm AS sieve, shall be compacted to a mean value of density ratio of not less than 97%. The calculation of density ratio shall be based on Standard compactive effort. A lot shall consist of a single layer of work. A minimum of 20% of all lots constructed shall be tested. | Test Results | Compaction Test | Test Result | TP |  | N/A |  | N/A
3.5 | Survey pick up / Bore Mark Out |  | During Bore | Survey to pick up as record of conformity on top of laid conduit prior to backfill. | Survey | Survey | AS Builts. | SCP | Foreman | N/A |  | N/A
4 | Completion
4.1 | Entry/ Exit Points |  | On Completion | Ensure clean fills is used to fill in Entry/ Exit points |  | Review | This ITP | IP | Foreman | N/A |  | N/A
4.2 | Conduit Layout |  | Each Lot | Conduit arrangement to suit trench detail; Conduit to slope towards pit for drainage purposes; Quantity of conduits to be confirmed and entered w/ each lot. | Utility Provider Drawings/ Project Plans | Project Engineer | Inspection | IP | Foreman | N/A |  | N/A
4.3 | Draw Cord |  | On Completion | Each conduit for electrical wiring an communications cables shall be provided one synthetic draw cord not less than 3mm diameter and a minimum breaking strain of 1.6kN | VR SS 733.05 | Inspection | This ITP | IP | Foreman | N/A |  | N/A
4.4 | Site clean up |  | On Completion | Ensure site is clean and all garbage has been removed | VR 733.09 | Inspection | This ITP | IP | Foreman | N/A |  | N/A
4.5 | Maintenance of Pavement |  | On Completion | The reinstated surface shall be maintained in a trafficable condition after the completion of backfilling. Additional pavement material shall be placed in the trench and compacted as specified where in paved areas settlement or loss of material from the surface exceeds 20 mm measured from a straight edge laid across the top of the trench. | VR 706.11 | Inspection | This ITP | IP | Foreman | N/A |  | N/A
4.6 | Records |  | On Completion | Bore Logs of the works to be supplied from subcontractor | Bore Logs | Document review | This ITP | HP* | Project Engineer | N/A |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
AP | Approval Point | Written or verbal approval given by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
WP | Witness Point | An inspection which must be witnessed by the Superintendent