## ITP Electrical Trenching
ITP Electrical Cable Trenching & Installation
Preconstruction
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
| Site Preparation | Visual inspection of cleared and levelled area | P,F,Attachment
Site free from debris, vegetation, and unevenness
| Survey and Marking | Alignment with approved IFC drawings & Digital Designs | P,F,Attachment
| Material Approval | Bedding and backfill sand complies with the specification notes for thermal resistivity | P,F,Attachment
Finger Trenching
| Trench Excavation | Finger trenches excavated to a minimum of 900 deep x 250mm wide
|  | Finger trench invert is smooth without stones or rocks protruding | P,F,NA
| Trench Bedding | Finger trench bedding consists of a minimum of 100mm of sand | P,F,NA
| Cable Installation | Cables installed in accordance with the IFC Drawings and specifications | P,F,NA
| Trench Backfill | Finger trenches shall include 75mm of sand over the cables | P,F,NA
|  | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables | P,F,NA
|  | 75mm of sand has been placed over the hard protective cover | P,F,NA
|  | Earth cables have been installed on the final layer of sand | P,F,NA
|  | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface | P,F,NA
|  | Existing excavated material is replaced and lightly compacted | P,F,NA
| Reinstatement | Finger trenches are reinstated back to tie into existing ground levels and contours | P,F,NA
Combined Services/DC Trenches
| Trench Excavation | Combined Services trenches are excavated to a minimum of 900 deep and wide enough to accommodate all of the cables required including minimum separation distances | P,F,NA
|  | Trench inverts are smooth without stones or rocks protruding | P,F,NA
| Trench Bedding | Combined Services trenches bedding consists of a minimum of 100mm of sand | P,F,NA
| Cable Installation | Cables installed in accordance with the IFC Drawings and specifications | P,F,NA
|  | Minimum separation distances are observed | P,F,NA
| Trench Backfill | Combined Services trenches shall include 75mm of sand over the cables | P,F,NA
|  | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables | P,F,NA
75mm of sand has been placed over the hard protective cover
Earth cables and comms ducts have been installed on the final layer of sand
Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
Existing excavated material is replaced and lightly compacted
| Reinstatement | Combined Services trenches are reinstated back to tie into existing ground levels and contours | P,F,NA
Comms & LV Trenches
| Trench Excavation | Comms/LV trenches are excavated to a minimum of 800 deep and 250mm wide | P,F,NA
|  | Trench inverts are smooth without stones or rocks protruding | P,F,NA
| Trench Bedding | Comms/LV trenches do not require bedding due to the cables being installed in conduit, but if rock is encountered, a minimum layer of 100mm of sand shall be placed | P,F,NA
| Cable Installation | Cables installed in accordance with the IFC Drawings and specifications | P,F,NA
|  | Minimum separation distances are observed | P,F,NA
Cables have been installed in conduit
| Pull Pit Installation | Pulling Pits are installed on a 100mm of Gap20 bedding | P,F,NA
|  | Pulling pits are installed on the line of the conduits | P,F,NA
|  | The tops of the pulling pits and level and clear of the road lane | P,F,NA
| Trench Backfill | Comms/LV trenches shall be completely backfilled with excavated trench material | P,F,NA
|  | Hard protection shall be installed over 75mm of backfill above the conduits | P,F,NA
|  | Soft warning tape is placed over the full extent of the conduits in the trench at a maximum of 400mm below the existing ground surface | P,F,NA
| Reinstatement | Comms/LV trenches are reinstated back to tie into existing ground levels and contours | P,F,NA
33kV AC Trenches
| Trench Excavation | AC trenches are excavated to a minimum of 1200 deep and wide enough to accommodate the three cables laid in a trefoil arrangement | P,F,NA
|  | Trench inverts are smooth without stones or rocks protruding | P,F,NA
| Trench Bedding | AC trenches bedding consists of a minimum of 100mm of sand | P,F,NA
| Cable Installation | Cables installed in accordance with the IFC Drawings and specifications | P,F,NA
|  | Minimum separation distances are observed of 1200mm to any other cable | P,F,NA
|  | Cables to be installed with minimum of 1200mm cover | P,F,NA
| Trench Backfill | AC trenches shall include 75mm of sand over the cables | P,F,NA
|  | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables | P,F,NA
|  | 75mm of sand has been placed over the hard protective cover | P,F,NA
|  | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface | P,F,NA
|  | Existing excavated material is replaced and lightly compacted | P,F,NA
| Reinstatement | AC trenches are reinstated back to tie into existing ground levels and contours | P,F,NA
Road Crossings
| Trench Excavation | Road crossing trenches are excavated to minimum widths and depths as described in the cross sections of the Electrical Drawings Minimum cover shall be: AC Cables - 1200mm DC Cables - 800mm Auxiliary/comms/lighting - 600mm | P,F,NA
|  | Trench inverts are smooth without stones or rocks protruding | P,F,NA
| Trench Bedding | Trench bedding consists of a minimum of 100mm of sand | P,F,NA
| Cable Installation | Cables installed in accordance with the IFC Drawings and specifications in 100mm HD Conduits - AC cables to be in 150mm conduits | P,F,NA
|  | Minimum separation distances are observed: 33kV - 1200mm DC Cables - 300mm more than 24 DC Cables a gap of 150mm in the middle Earth cables - 150mm | P,F,NA
| Trench Backfill | Road Crossings trenches shall include 150mm of sand over the conduit | P,F,NA
|  | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables | P,F,NA
|  | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface | P,F,NA
|  | Backfilled material shall excavated trench material backfilled and compacted to 95% native soil density | P,F,NA
|  | Existing excavated material is replaced and lightly compacted | P,F,NA
| Reinstatement | AC trenches are reinstated back to tie into existing ground levels and contours | P,F,NA
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive inspection of all elements relating to the RMU Drainage
Compliance with IFC drawings and specifications
|  | Verify all Drainage meets design and functional requirements | Holdpoint United Civil & CHINT, P,F,Attachment
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor | P,F,Attachment
| Documentation | On completion of the RMU Drainage | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | Holdpoint United Civil & CHINT, P,F,Attachment
Complete and approved by client