## ITP RMU Slabs
RMU BUILDING SLAB ITP
P,F,Attachment is a term used when digitised so the company digitising the ITP knows it is a Pass/Fail/NZ Check box and or a hold point and for who.
Preconstruction
| Location | Location of Foundation Construction | Textbox
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
United Civil Hold Point
| Survey & Setout | Visual Inspection of RMU Location setout
|  | Benchmark established as a dataum for levels | P,F,Attachment
|  | Alignment with approved drawings and site plan | United Civil Hold Point
| Calibration of Plant | All testing and measuring equipment calibration certificates valid | P,F,Attachment
| Site Clearing | Visual inspection of cleared area | P,F,Attachment
Free from vegetation, debris, and obstructions
Material Procurement
| Review of Concrete, and Reinforcement steel | Compliance with IFC Drawings, Specifications and Standards
All reinforcing bars shall be deformed grade 300 to AS/NZS 4671
All concrete construction shall be in accordance with NZS3109
Geogrid and Bidim to minimum Class B
Concrete strength shall be a minimum of 25MPa
Delivery Dockets supplied for each delivery/Pour
|  | Material test certificates supplied for reinforcing steel | P,F,Attachment | United Civil/CHINT Hold Point
Construction - Slab Foundation
| Excavation to Subgrade | Relevant Specification: IFC Drawings
Test Method: Visual inspection and photos
Timing/Frequency: Visual Inspection of the foundation
|  | Acceptance Criteria: No organic or unsuitable material is present Foundation is at the correct level | P,F,Attachment
| Foundation Subbase Construction | Relevant Specification: IFC Drawings
Test Method: Photos and dimensional check that the construction and RL's comply with the IFC Drawings Minimum of 200mm of compacted Gap40 over Geogrid and Bidim Test the foundation layers strength with a Clegg Hammer
Timing/Frequency: 4x sets of Clegg Hammer tests and measurements to determine the compaction of foundation layers
|  | Acceptance Criteria: Visual Inspection and photos of compacted aggregate and tests Thickness of Gap40 shall be 200mm over bidim and geogrid as directed Clegg hammer tests shall meet a minimum CIV of 24 on the 4th blow for each test | P,F,Attachment | United Civil & Chint Hold Point
Construction - Concrete
| Prepour Inspection | FORMWORK & REINFORCING INSTALLATION
Relevant Specification: IFC Drawings Steel Reinforcing shall comply with NZS3109 Concrete formwork construction shall comply with NZS3104 & 3109
Test Method: Visual and dimensional check that the construction and minimum cover required complies with the IFC Drawings & Specifications and Standards
|  | Timing/Frequency: Prior to pouring |  |  | 29228
|  | Acceptance Criteria: Formwork shall be free of warps, bends or kinks, and the tolerances of the top surface of the form shall ensure compliance with the finished floor tolerances of +/- 10mm Reinforcing materials - hooks, bends, bars and surface condition of reinforcement, spacing and fixing, splices, cover and placing tolerances shall comply with NZS3109 unless modified in the IFC drawings Prepour Inspection completed and filled in | P,F,Attachment | CHINT & United Civil Hold Point | 1.716
EMBEDMENTS
Relevant Specification: IFC Drawings
Test Method: Visual inspection, photos and dimensional check that any embedments comply with the IFC Drawings
Timing/Frequency: When installed and prior to pouring
|  | Acceptance Criteria: Embeded items are installed to meet expected outcomes against the IFC drawings Noted in the Prepour Inspection ITC | P,F,Attachment | United Civil Hold Point
| Concrete Mixing | Relevant Specification: IFC Drawings NZS3104
Timing/Frequency: Prior to and for each pour
|  | Acceptance Criteria: Concrete baching plant is certified to batch concrete under NZS3104 Concrete strength to be 25MPa Concrete mix delivery dockets | P,F,Attachment
| Concrete Placement | Test Method: Visual Inspection during pouring
Timing/Frequency: During each pour
|  | Acceptance Criteria: Proper compaction of poured concrete, no segregatation or honey combing | P,F,Attachment
| Slump & Strength Testing | Relevant Specification: Tests taken in accordance with NZS3112.2
Test Method: Slump Testing Cylinder compression testing
Timing/Frequency: Slump Tests are prior to pouring Compression testing shall be at 7, 14 & 28 days post pouring
|  | Acceptance Criteria: Slump shall be 100 & Compression testing shall be a minimum of 25MPa at 28 days post pouring Test report/dockets shall be supplied | P,F,Attachment
Post Construction
| Curing & Surface Finish | Relevant Specification: IFC Drawings NZS3104 & NZS3109
Test Method: Visual Inspection of curing concrete Curing concrete shall remain damp during the curing period
Timing/Frequency: Slump Tests are prior to pouring Compression testing shall be a set of 3 cylinders taken from freshly batched concrete and tested in accordance with NZS3112
|  | Acceptance Criteria: Slump shall be 100 & Compression testing shall be a minimum of 25MPa at 28 days post pouring Test report/dockets shall be supplied | P,F,Attachment
| Surface Finish | Test Method: Visual Inspection of surface for cracks, voids, and finish quality
|  | Acceptance Criteria: No visible defects or honeycombing for each foundation post striking of formwork | P,F,Attachment
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive inspection of all elements relating to the concrete foundations
Compliance with IFC drawings and specifications
Verify concrete foundations meet design and functional requirements from the IFC drawings to what was constructed
|  | Concrete Foundations ready for subsequent construction activities | P,F,Attachment | CHINT Hold Point & United Civil Hold Point
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor | P,F,Attachment
| Documentation | On completion of the concrete foundations:
|  | Submission of all test results, ITC's and any as-built drawings | P,F,Attachment
|  | Complete and approved by client | United Civil Hold Point

## ITC Concrete Prepour
ITC Concrete Prepour
Preconstruction | Design Drawings | Contract Name | Text Box
|  | Contract Number | Text Box
|  | Location | Text Box
|  | Lot Number | Text Box
|  | Description of Pour | Text Box
|  | Issued for Construction Drawings available | P,F, N/A, Comment
Construction | Formwork | Formwork/ Moulds Braced and Secure | P,F, N/A, Comment
|  | Dimensional Check Completed | P,F, N/A, Comment
|  | Formwork/ Moulds Within Tolerances | P,F, N/A, Comment
|  | Formwork/ Mould Surfaces in Good Condition | P,F, N/A, Comment
|  | Chamfers in Place as Per IFC/ Shop Drawings | P,F, N/A, Comment
|  | Formwork/ Mould Release agent Used | P,F, N/A, Comment
|  | Construction Joints Allowed For | P,F, N/A, Comment
|  | Penetrations Set Out as Per IFC/ Shop Drawings | P,F, N/A, Comment
|  | Cast In Hardware as Per IFC/ Shop Drawings | P,F, N/A, Comment
|  | Surface Finish Meets Specification | P,F, N/A, Comment
| Steel Reinforcing | Reinforcing Braced and Secure | P,F, N/A, Comment
|  | Dimensional Checks Completed | P,F, N/A, Comment
|  | Bar Diameters as Per IFC/ Shop Darwings | P,F, N/A, Comment
|  | No. of Bars as Per IFC/ Shop Drawings | P,F, N/A, Comment
|  | Bar Spacings as Per IFC/ SHop Drawings | P,F, N/A, Comment
|  | Cover as Per IFC/ Shop Drawings | P,F, N/A, Comment
|  | Lap Lengths as Per Specifications | P,F, N/A, Comment
|  | Lifting Hardware as Per IFC/ Shop Drawings | P,F, N/A, Comment
| Concrete | Concrete as Per Approved Mix Design | P,F, N/A, Comment
|  | Strength Required | Text Box & P,F,NZ, Comment
|  | Slump Tests Undertaken onsite | P,F, N/A, Comment
|  | Test Cylinders Taken | P,F, N/A, Comment
|  | Surface Finish as Per Specifications | P,F, N/A, Comment
|  | Construction Joints - Surface Preparation Completes | P,F, N/A, Comment
|  | Additional Curing Measures Required | P,F, N/A, Comment
|  | Client / Engineer Inspection Required | P,F, N/A, Comment
| Pre-Pour Checked and Accepted |  | Hold Point, P ,F , N/A , Comment
|  | Date of Inspection | Date text box
| Documentation | On completion of the Light Pole foundations: | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | United Civil Hold Point
Complete and approved by client