## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Electrical Cable Trenching & Installation | itp
section | Preconstruction
checkpoint | Design Drawings
label | Issued for Construction Drawings available
checkpoint | Site Preparation
label | Visual inspection of cleared and levelled area
label | Site free from debris, vegetation, and unevenness
checkpoint | Survey and Marking
label | Alignment with approved IFC drawings & Digital Designs
checkpoint | Material Approval
label | Bedding and backfill sand complies with the specification notes for thermal resistivity
section | Finger Trenching - Trench Excavation
checkpoint | Trench Excavation
label | Finger trenches excavated to a minimum of 900 deep x 250mm wide
label | Finger trench invert is smooth without stones or rocks protruding
section | Finger Trenching - Trench Bedding
checkpoint | Finger trench bedding consists of a minimum of 100mm of sand
section | Finger Trenching - Cable Installation
checkpoint | Cables installed in accordance with the IFC Drawings and specifications
section | Finger Trenching - Trench Backfill
checkpoint | Finger trenches shall include 75mm of sand over the cables
checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
checkpoint | 75mm of sand has been placed over the hard protective cover
checkpoint | Earth cables have been installed on the final layer of sand
checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
checkpoint | Existing excavated material is replaced and lightly compacted
section | Finger Trenching - Reinstatement
checkpoint | Finger trenches are reinstated back to tie into existing ground levels and contours
section | Combined Services/DC Trenches - Trench Excavation
checkpoint | Combined Services trenches are excavated to a minimum of 900 deep and wide enough to accommodate all of the cables required including minimum separation distances
checkpoint | Trench inverts are smooth without stones or rocks protruding
section | Combined Services/DC Trenches - Trench Bedding
checkpoint | Combined Services trenches bedding consists of a minimum of 100mm of sand
section | Combined Services/DC Trenches - Cable Installation
checkpoint | Cables installed in accordance with the IFC Drawings and specifications
checkpoint | Minimum separation distances are observed
section | Combined Services/DC Trenches - Trench Backfill
checkpoint | Combined Services trenches shall include 75mm of sand over the cables
checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
label | 75mm of sand has been placed over the hard protective cover
label | Earth cables and comms ducts have been installed on the final layer of sand
label | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
label | Existing excavated material is replaced and lightly compacted
section | Combined Services/DC Trenches - Reinstatement
checkpoint | Combined Services trenches are reinstated back to tie into existing ground levels and contours
section | Comms & LV Trenches - Trench Excavation
checkpoint | Comms/LV trenches are excavated to a minimum of 800 deep and 250mm wide
checkpoint | Trench inverts are smooth without stones or rocks protruding
section | Comms & LV Trenches - Trench Bedding
checkpoint | Comms/LV trenches do not require bedding due to the cables being installed in conduit, but if rock is encountered, a minimum layer of 100mm of sand shall be placed
section | Comms & LV Trenches - Cable Installation
checkpoint | Cables installed in accordance with the IFC Drawings and specifications
checkpoint | Minimum separation distances are observed
label | Cables have been installed in conduit
section | Comms & LV Trenches - Pull Pit Installation
checkpoint | Pulling Pits are installed on a 100mm of Gap20 bedding
checkpoint | Pulling pits are installed on the line of the conduits
checkpoint | The tops of the pulling pits and level and clear of the road lane
section | Comms & LV Trenches - Trench Backfill
checkpoint | Comms/LV trenches shall be completely backfilled with excavated trench material
checkpoint | Hard protection shall be installed over 75mm of backfill above the conduits
checkpoint | Soft warning tape is placed over the full extent of the conduits in the trench at a maximum of 400mm below the existing ground surface
section | Comms & LV Trenches - Reinstatement
checkpoint | Comms/LV trenches are reinstated back to tie into existing ground levels and contours
section | 33kV AC Trenches - Trench Excavation
checkpoint | AC trenches are excavated to a minimum of 1200 deep and wide enough to accommodate the three cables laid in a trefoil arrangement
checkpoint | Trench inverts are smooth without stones or rocks protruding
section | 33kV AC Trenches - Trench Bedding
checkpoint | AC trenches bedding consists of a minimum of 100mm of sand
section | 33kV AC Trenches - Cable Installation
checkpoint | Cables installed in accordance with the IFC Drawings and specifications
checkpoint | Minimum separation distances are observed of 1200mm to any other cable
checkpoint | Cables to be installed with minimum of 1200mm cover
section | 33kV AC Trenches - Trench Backfill
checkpoint | AC trenches shall include 75mm of sand over the cables
checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
checkpoint | 75mm of sand has been placed over the hard protective cover
checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
checkpoint | Existing excavated material is replaced and lightly compacted
section | 33kV AC Trenches - Reinstatement
checkpoint | AC trenches are reinstated back to tie into existing ground levels and contours
section | Post Construction and Handover - Final Walkthrough & Inspection
checkpoint | Final Walkthrough & Inspection
label | Comprehensive inspection of all elements relating to the RMU Drainage
label | Compliance with IFC drawings and specifications
label | Verify all Drainage meets design and functional requirements
holdpoint | United Civil & CHINT Hold Point
section | Post Construction and Handover - Non-Conformance-Reports
checkpoint | Each Non-Conformance Reported, Rectified & Closed Out
section | Post Construction and Handover - Punch List
checkpoint | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely mannor
section | Post Construction and Handover - Documentation
checkpoint | Documentation
label | On completion of the RMU Drainage
label | Submission of all test results, ITC's and any as-built drawings
label | Complete and approved by client
holdpoint | United Civil & CHINT
checklist | ITP - Concrete Foundations | itp
section | Preconstruction
checkpoint-no-status | Design Drawings
textbox | Contract Name
textbox | Contract Number
textbox | Location
textbox | Lot Number
textbox | Description of Pour
checkpoint | Issued for Construction Drawings available
section | Construction - Formwork
checkpoint | Formwork/ Moulds Braced and Secure
checkpoint | Dimensional Check Completed
checkpoint | Formwork/ Moulds Within Tolerances
checkpoint | Formwork/ Mould Surfaces in Good Condition
checkpoint | Chamfers in Place as Per IFC/ Shop Drawings
checkpoint | Formwork/ Mould Release agent Used
checkpoint | Construction Joints Allowed For
checkpoint | Penetrations Set Out as Per IFC/ Shop Drawings
checkpoint | Cast In Hardware as Per IFC/ Shop Drawings
checkpoint | Surface Finish Meets Specification
section | Construction - Steel Reinforcing
checkpoint | Reinforcing Braced and Secure
checkpoint | Dimensional Checks Completed
checkpoint | Bar Diameters as Per IFC/ Shop Darwings
checkpoint | No. of Bars as Per IFC/ Shop Drawings
checkpoint | Bar Spacings as Per IFC/ SHop Drawings
checkpoint | Cover as Per IFC/ Shop Drawings
checkpoint | Lap Lengths as Per Specifications
checkpoint | Lifting Hardware as Per IFC/ Shop Drawings
section | Construction - Concrete
checkpoint | Concrete as Per Approved Mix Design
checkpoint | Strength Required
textbox | Strength:
checkpoint | Slump Tests Undertaken onsite
checkpoint | Test Cylinders Taken
checkpoint | Surface Finish as Per Specifications
checkpoint | Construction Joints - Surface Preparation Completes
checkpoint | Additional Curing Measures Required
checkpoint | Client / Engineer Inspection Required
section | Construction - Pre-Pour Checked and Accepted
checkpoint | Pre-Pour Checked and Accepted
date | Date of Inspection
holdpoint | HOLD POINT