## Folder Structure
Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 | Instruction to CONQA | Checklist Name
Illuka Resources Mud System 1 J#37445
Mud City
Instruments
|  |  | PIT-02500 - MP01-M02-SC-004 PRESSURE TX |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | PIT-02501 - MP01-M02-PU-040 DESILTER CYCLONE FEED PUMP #1 DISCHARGE PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | PIT-02502 - MP01-M02-PU-041 CENTRIFUGE PUMP #1 DISCHARGE PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | PIT-02503 - MP01-M02-PU-042 PRESSURE TX |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | LIT-02504 - MP01-M02-TK040 LEVEL TX |  | please add: | ITR-I-16 Level Instrument Installation
|  |  | LIT-02505 - MP01-M02-TK041 LEVEL TX |  | please add: | ITR-I-16 Level Instrument Installation
|  |  | LIT-02506 - MP01-M02-TK042 LEVEL TX |  | please add: | ITR-I-16 Level Instrument Installation
|  |  | FS-02515 - CENTRIFUGE FEED PUMP DISCHARGE |  | please add: | ITR-I-14 Flow Meter Installation
|  |  | FIT-X2040 - RECYCLER FLOW TX |  | please add: | ITR-I-14 Flow Meter Installation
|  |  | PIT-02520 - MP01-M02-PU-049 MUD MIX PUMP #1 DISCHARGE PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | PIT-02521 - MP01-M02-PU-048 MUD MIX PUMP #2 DISCHARGE PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | LIT-02522 - MP01-M02-TK048 LEVEL TX |  | please add: | ITR-I-16 Level Instrument Installation
|  |  | LIT-02523 - MP01-M02-TK049 LEVEL TX |  | please add: | ITR-I-16 Level Instrument Installation
Cables
|  |  | PU040-LV052-I2 - 1.5mm2 1PR R1-DEXN-1P1.5BK |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PU040-LV052-P3 - 35mm2 4G35+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU042-LV052-I2 - 1.5mm2 1PR R1-DEXN-1P1.5BK |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU042-LV052-P3 - 50mm2 4G50+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC001-LV052-P2 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC001-LV052-P4 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC002-LV052-P2 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC002-LV052-P4 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC003-LV052-P2 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC003-LV052-P4 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC004-LV052-P2 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | SC004-LV052-P4 - 2.5mm2 4G2.5+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG040-LV052-P2 - 10mm2 4G10+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG041-LV052-P2 - 10mm2 4G10+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG042-LV052-P2 - 10mm2 4G10+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU049-LV052-I2 - 1.5mm2 1PR R1-DEXN-1P1.5BK |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU049-LV052-P3 - 50mm2 4G50+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU048-LV052-I2 - 1.5mm2 1PR R1-DEXN-1P1.5BK |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU048-LV052-P3 - 50mm2 4G50+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG048-LV052-P2 - 10mm2 4G10+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG049-LV052-P2 - 10mm2 4G10+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | CV001-LV052-P2 - 4mm2 4G4+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST050LCS-JB1-C2 - 1.5mm2 34G1.5 ROBUST 215 C |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST051LCS-JB1-C2 - 1.5mm2 34G1.5 ROBUST 215 C |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST051LCS-JB1-C4 - 1.5mm2 25G1.5 ROBUST 215 C |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST051-DB052-P2 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST051-DB052-P4 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST051-DB052-P6 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | MTR1-CP001-P2 - 16mm2 4G16 |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU041-CP001-P2 - 0mm2 4G50+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | MTR2-CP001-P2 - 10mm2 4G10+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | IJB-CP001-I2 - 1.5mm2 18G1.5 FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | LQ012-LV052-P2 - 10mm2 4G10+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | WTXXXX-PLC052-P2 - 1.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | LIT02003-PLC052-I2 - 1.5mm2 2PR |  | please add: | ITR-I-21 - Instrument Cables
|  |  | ST050IJB1-PLC052-I2 - 1.5mm2 8PR R1-DEXN-8P1.5BK |  | please add: | ITR-I-21 - Instrument Cables
|  |  | ST051IJB1-PLC052-I2 - 1.5mm2 8PR R1-DEXN-8P1.5BK |  | please add: | ITR-I-21 - Instrument Cables
|  |  | BAM-CTV-001-D2 - CAT 6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PIT02500-ST051IJB01-I1 - 1.5mm2 1PRR1-DEXN-1P1.5BK 1.5MM 1PR |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02500-ST051IJB01-I2 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02501-ST051IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02502-ST051IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02503-ST051IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LIT02504-ST051IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LIT02505-ST051IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LIT02506-ST051IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | FS02515-ST051IJB01-I1 - 1.5mm2 2PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | FITX2040-ST050IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02520-ST050IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02521-ST050IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LIT02522-ST050IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LIT02523-ST050IJB01-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
Cable Support
|  |  | Underground Cable Support |  | please add: | ITR-E-02A Conduit/Ducting Below Ground
|  |  | Above Ground Cable Support |  | please add: | ITR-E-02B Cable Supports Above Ground
Electrical Equipment
Junction Boxes
|  |  |  | IJB-001 - Mud Recycling Skid Junction Box | please add: | ITR-E-07 - Junction Box
|  |  |  | IJB-002 - Mixing Tank Skid Junction Box | please add: | ITR-E-07 - Junction Box
Decontactors
|  |  |  | IJB-001 - PIT-02500 - Outlet | please add: | ITR-E-01 General Electrical Equipment
Local Control Station
|  |  |  | LCS - Recyler Tank | please add: | ITR-E-45 Local Control Station
|  |  |  | LCS - Mixing Tank | please add: | ITR-E-45 Local Control Station
Motors
|  |  |  | Shaker 1 - MP01-M02-SC001 A | please add: | ITR-E-13 Motors
|  |  |  | Shaker 1 - MP01-M02-SC001 B | please add: | ITR-E-13 Motors
|  |  |  | Shaker 2 - MP01-M02-SC002 A | please add: | ITR-E-13 Motors
|  |  |  | Shaker 2 - MP01-M02-SC002 B | please add: | ITR-E-13 Motors
|  |  |  | Shaker 3 - MP01-M02-SC003 A | please add: | ITR-E-13 Motors
|  |  |  | Shaker 3 - MP01-M02-SC003 B | please add: | ITR-E-13 Motors
|  |  |  | Shaker 4 - MP01-M02-SC004 A | please add: | ITR-E-13 Motors
|  |  |  | Shaker 4 - MP01-M02-SC004 B | please add: | ITR-E-13 Motors
|  |  |  | Desilter Feed Pump - MP01-M02-PU040 | please add: | ITR-E-13 Motors
|  |  |  | Mud Transfer Pump #1 - MP01-M02-PU042 | please add: | ITR-E-13 Motors
|  |  |  | Recycle Tank Agitator 1 - MP01-M02-AG040 | please add: | ITR-E-13 Motors
|  |  |  | Recycle Tank Agitator 2 - MP01-M02-AG041 | please add: | ITR-E-13 Motors
|  |  |  | Recycle Tank Agitator 3 - MP01-M02-AG042 | please add: | ITR-E-13 Motors
|  |  |  | Mud Mix Pump #1 - MP01-M02-PU049 | please add: | ITR-E-13 Motors
|  |  |  | Mud Mix Transfer Pump #2 - MP01-M02-PU048 | please add: | ITR-E-13 Motors
|  |  |  | Mixing Tank Agitator 1 - MP01-M02-AG048 | please add: | ITR-E-13 Motors
|  |  |  | Mixing Tank Agitator 2 - MP01-M02-AG049 | please add: | ITR-E-13 Motors
|  |  |  | Mixing Tank Screw Conveyor - MP01-M02-CV001 | please add: | ITR-E-13 Motors
Lighting
|  |  |  | Lighting Internal SWR | please add: | ITR-E-48 General Lighting
|  |  |  | Lighting Emergency/Exit SWR | please add: | ITR-E-48 General Lighting
|  |  |  | External Lighting 1 | please add: | ITR-E-48 General Lighting
|  |  |  | External Lighting 2 | please add: | ITR-E-48 General Lighting
Earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
Active Tank 01
Instruments
|  |  | LIT-02511 - MP01-M02-TK044 LEVEL TX 1 |  | please add: | ITR-I-16 Level Instrument Installation
|  |  | PIT-02513 - MP01-M02-TK044 CHARGE PUMP #1 DISCHARGE PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | PIT-02514 - MP01-M02-TK044 CHARGE PUMP #1 SUCTION PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | TIT-02 - MP01-M02-ST055 ROOM TEMPERATURE |  | please add: | ITR-I-13 Temperature Instrument Installation
Cables
|  |  | PU044-LV055-P1 - 50mm2 3x35+E10 FIRSTFLEX CU/X90/SPVC |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU044-LV055-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PU044-LV055-C1 - 1.5mm2 16C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU044-LV055-P2 - 50mm2 4G35+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU044-LV055-C2 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU025-LV055-P1 - 50mm2 3x35+E10 FIRSTFLEX CU/X90/SPVC |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU025-LV055-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PU025-LV055-C1 - 1.5mm2 16C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU025-LV055-P2 - 50mm2 4G35+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU025-LV055-C2 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG044-LV055-P1 - 3PH+E (10mm2) |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG044-LV055-C1 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG045-LV055-P1 - 3PH+E (10mm2) |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG045-LV055-C1 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PLC055-LV055-P1 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST055-LV055-P1 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST055-LV055-P2- 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST055-LV055-P3 - 2PH+E (6mm2) 6mm2 |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST055-LV055-P4 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST055-LV055-P5 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST055-LV055-P6 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | LIT-02511-PLC055-1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT-02514-PLC055-1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT-02513-PLC055-1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LV055-PLC055-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LV055-PLC055-I2 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | SD1-PLC055-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LV055-PLC055-I3 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | TIT02-PLC055-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | - 4x95+E35 95mm2 |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | - 4x95+E35 95mm2 |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | MP01-LV055-FB01/01 - SMOF LC-LC |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | - SMOF LC-LC |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/1 - NSA001-1/3 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/2 - NSA001-1/4 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/3 - NSA001-1/5 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/4 - NSA001-1/6 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
Cable Support
|  |  | Underground Cable Support |  | please add: | ITR-E-02A Conduit/Ducting Below Ground
|  |  | Above Ground Cable Support |  | please add: | ITR-E-02B Cable Supports Above Ground
Electrical Installations
Motors
|  |  |  | Rig Active Charge Pump - MP01-M02-PU044 | please add: | ITR-E-13 Motors
|  |  |  | Active Tank Sump Pump #1 -MP01-M02-PU025 | please add: | ITR-E-13 Motors
|  |  |  | Active Tank Agitator #1 - MP01-M02-AG044 | please add: | ITR-E-13 Motors
|  |  |  | Active Tank Agitator #2 - MP01-M02-AG045 | please add: | ITR-E-13 Motors
Local Control Stations
|  |  |  | Active Tank 1 LCS | please add: | ITR-E-45 Local Control Station
Decontactors
|  |  |  | Active Tank 01 Sump Pump #1 - Outlet | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Tank 01 LCS - Outlet | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Tank 01 Sump Pump #1 Thermistor - Outlet | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Tank 01 Incomer - Outlet | please add: | ITR-E-01 General Electrical Equipment
Switchroom
|  |  |  | HVAC - AC01 | please add: | ITR-E-55 HVAC System
|  |  |  | Fire Protection System | please add: | ITR-E-56 Fire Detection System
|  |  |  | Power Outlets | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Light Switches | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Charge Pump VSD - MP01-M02-PU044-VSD | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Sump Pump VSD - MP01-M02-PU025-VSD | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Electrical Switchroom | please add: | ITR-E-09 Electrical Switch Rooms
Lighting
|  |  |  | Internal Lighting | please add: | ITR-E-48 General Lighting
|  |  |  | External Lighting | please add: | ITR-E-48 General Lighting
Earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
Active Tank 02
Instruments
|  |  | LIT-02531 - MP01-M02-TK046 LEVEL TX 1 |  | please add: | ITR-I-16 Level Instrument Installation
|  |  | LIT-02532 - MP01-M02-TK047 LEVEL TX 1 |  | please add: | ITR-I-16 Level Instrument Installation
|  |  | PIT-02533 - MP01-M02-TK047 CHARGE PUMP #3 DISCHARGE PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | PIT-02534 - MP01-M02-TK047 CHARGE PUMP #3 SUCTION PRESSURE TRANSMITTER |  | please add: | ITR-I-15 Pressure Instrument Installation
|  |  | TIT-03 - MP01-M02-ST056 ROOM TEMPERATURE |  | please add: | ITR-I-13 Temperature Instrument Installation
Cables
|  |  | PU046-LV056-P1 - 35mm2 3x35+E10 FIRSTFLEX CU/X90/SPVC |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU046-LV056-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PU046-LV056-C1 - 1.5mm2 16C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU046-LV056-P2 - 50mm2 4G35+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU046-LV056-C2 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU026-LV056-P1 - 35mm2 3x35+E10 FIRSTFLEX CU/X90/SPVC |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU026-LV056-I1 - 1.5mm2 1PR/D |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PU026-LV056-C1 - 1.5mm2 16C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU026-LV056-P2 - 35mm2 4G35+(2x1.5) SERVO FD 796 CP |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PU026-LV056-C2 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG046-LV056-P1 - 3PH+E (10mm2) |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG046-LV056-C1 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG047-LV056-P1 - 3PH+E (10mm2) |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | AG047-LV056-C1 - 1.5mm2 6C+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | PLC056-LV056-P1 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST056-LV056-P1 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST056-LV056-P2- 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST056-LV056-P3 - 2PH+E (6mm2) 6mm2 |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST056-LV056-P4 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST056-LV056-P5 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | ST056-LV056-P6 - 2.5mm2 2PH+E |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | LIT02531-PLC056-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LIT02532-PLC056-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02534-PLC056-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | PIT02533-PLC056-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LV056-PLC056-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | SD02-PLC056-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | LV056-PLC056-I2 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | TIT03-PLC056-I1 - 1PR/D 1.5mm2 |  | please add: | ITR-I-21 - Instrument Cables
|  |  | - 4x95+E35 95mm2 |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | - 4x95+E35 95mm2 |  | please add: | ITR-E-05 - Low Voltage Cable
|  |  | MP01-LV056-FB01/01 - SMOF LC-LC |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | - SMOF LC-LC |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/1 - NSA001-1/3 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/2 - NSA001-1/4 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/3 - NSA001-1/5 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
|  |  | PP1/4 - NSA001-1/6 - CAT6 |  | please add: | ITR-E-29 Cat 6 Communication Cable
Cable Support
|  |  | Underground Cable Support |  | please add: | ITR-E-02A Conduit/Ducting Below Ground
|  |  | Above Ground Cable Support |  | please add: | ITR-E-02B Cable Supports Above Ground
Electrical Installations
Motors
|  |  |  | Rig Active Charge Pump - MP01-M02-PU044 | please add: | ITR-E-13 Motors
|  |  |  | Active Tank Sump Pump #1 -MP01-M02-PU025 | please add: | ITR-E-13 Motors
|  |  |  | Active Tank Agitator #1 - MP01-M02-AG044 | please add: | ITR-E-13 Motors
|  |  |  | Active Tank Agitator #2 - MP01-M02-AG045 | please add: | ITR-E-13 Motors
Local Control Stations
|  |  |  | Active Tank 2 LCS | please add: | ITR-E-45 Local Control Station
Decontactors
|  |  |  | Active Tank 02 Sump Pump #2 - Outlet | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Tank 2 LCS - Outlet | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Tank 02 Sump Pump #2 Thermistor - Outlet | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Tank 02 Incomer - Outlet | please add: | ITR-E-01 General Electrical Equipment
Switchroom
|  |  |  | HVAC - AC02 | please add: | ITR-E-55 HVAC System
|  |  |  | Fire Protection System | please add: | ITR-E-56 Fire Detection System
|  |  |  | Power Outlets | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Light Switches | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Charge Pump VSD - MP01-M02-PU046-VSD | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Active Sump Pump - MP01-M02-PU026-VSD | please add: | ITR-E-01 General Electrical Equipment
|  |  |  | Electrical Switchroom | please add: | ITR-E-09 Electrical Switch Rooms
Lighting
|  |  |  | Internal Lighting | please add: | ITR-E-48 General Lighting
|  |  |  | External Lighting | please add: | ITR-E-48 General Lighting
Earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing
|  |  | Earthing Cables |  | please add: | ITR-E-12 Electrical earthing

## Checklists
Type | Name | Values | Prefix | Postfix | Usage Count | User Addable | Template Name
checklist | ITR-E-01 General Electrical Equipment
checkpoint | General Electrical Equipment
textbox | Type of Electrical Equipment:
textbox | Make, Model, Manufacturer, Serial No. (if applicable):
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Installation is clean and tidy | Yes,N/A
button | Mounting arrangement correct | Yes,N/A
button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
button | External cabling is correctly installed and labelled. | Yes,N/A
button | Check that Equipment is correctly earthed. | Yes,N/A
button | Check gland, plate, frame & door earth continuity | Yes,N/A
button | All spare entries blanked off with correct plugs. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Conforms to Specifications and Drawings. | Yes,N/A
button | As-builts complete. | Yes,N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  | MegaOhms
signoff | Installed by:
checklist | ITR-E-02A Conduit/Ducting Below Ground
checkpoint | Conduit/Ducting Installation Below Ground
button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
button | Check all fixings are tight and secure. | Yes,N/A
button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
button | As-builts complete. | Yes,N/A
signoff | Installed by:
checklist | ITR-E-02B Cable Supports Above Ground
checkpoint | Cable Supports Above Ground
button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
button | All covers fitted if applicable. | Yes,N/A
button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
button | Splice plates, barriers, earthing system secure. | Yes,N/A
button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
button | Cables have adequate mechanical protection as and where required. | Yes,N/A
button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
button | Tray bonded to structure at correct locations. | Yes,N/A
button | Earth bonding continuity tested – record result: | Yes,N/A
button | As-builts complete. | Yes,N/A
signoff | Installed by:
checklist | ITR-E-02C Cable Transits
checkbox | Cable Transits
button | Transit frame installed as per drawings. | Yes,N/A
button | Transit frame identification marked correctly and visible. | Yes,N/A
button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
button | Rated insulation installed to transit (where required.) | Yes,N/A
button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
button | Cables pass through frames without strain on blocks. | Yes,N/A
button | All cables identified on both sides of transit and visible. | Yes,N/A
button | As-builts complete. | Yes,N/A
signoff | Installed by:
checklist | ITR-E-03 Entec - Distribution Board Installation
checkpoint - Mandatory photo | Distribution Board Installation
button | Inspect for mechanical damage from freight and handling | Yes,N/A
button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
checkpoint | Test Results
textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  | MegaOhms
textbox | Earth Continuity |  |  | Ohms
textbox | Earth Bond |  |  | Ohms
textbox | Fault Loop Impedance, PSSC.
textbox | RCD Test results (1/2x I, 1x I, 5x I)
textbox | Voltage and Phase Rotation
button | As-builts complete. | Yes,N/A
signoff | Installed by:
checklist-flat | ITR-E-05 - Low Voltage Cable
checkpoint | Low Voltage Cable
button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
button | Check dressing / cleating, cable undamaged | Yes,N/A
button | Check cable cores correctly identified and labelled. | Yes,N/A
button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
button | Check Armour / Screen correctly made off. | Yes,N/A
button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
button | Glanding / Locknuts correctly installed. | Yes,N/A
textbox | Gland type - from: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Gland type - to: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
checklist | ITR-E-06 Control Panel
checkpoint | Control Panel
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Check holding down/mounting arrangement is correct. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Check tightness of circuit connections. | Yes,N/A
button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
button | Ammeter scale and current transformer correct. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
button | Heaters correctly installed. | Yes,N/A
button | Fuse rating correct. | Yes,N/A
button | As-builts complete. | Yes,N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
checklist-flat | ITR-E-07 - Junction Box
checkpoint | Junction Box
button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
button | Check mechanical damage | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Earthing installed correctly and as per drawing | Yes,N/A
button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
button | Check all Cables & Cores are correctly identified | Yes,N/A
button | Check internals for cleanliness | Yes,N/A
button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
checkpoint | Tests
textbox | Record earth bar resistance to earth bond
textbox | All other relevant tests:
button | As-builts complete. | Yes,N/A
signoff | Installed by:
checklist | ITR-E-08 Heat Tracing Circuit
checkpoint | Heat Tracing Circuit
button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
button | End caps and connection kits correctly installed. | Yes,N/A
button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
button | All spare entries blanked off correctly. | Yes,N/A
textbox | IR test: Phase - Earth, Phase - Neutral | Yes,N/A
button | Equipment certification meets the area classification requirements. | Yes,N/A
button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | As-builts complete. | Yes,N/A
checkpoint | Electrical tests
textbox | Insulation Resistance: Phase - Earth
textbox | Insulation Resistance: Phase - Neutral
signoff | Installed by:
checklist | ITR-E-09 Electrical Switch Rooms
checkpoint - Mandatory photo | Electrical Switchroom
button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
button | Ensure there is no visible damage to installed equipment. | Yes,N/A
button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
button | Check internals for cleanliness | Yes,N/A
button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
button | As-builts complete | Yes,N/A
signoff | Installed by:
checklist | ITR-E-10 Electrical Equipment Package
checkpoint | Electrical Equipment Package
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check equipment is correctly rated for the area. | Yes,N/A
button | Check if package is complete with all accessories. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | All transportation supports, stops and fastenings removed. | Yes,N/A
button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
button | Check package is installed on a level plane. | Yes,N/A
button | External cabling (if required) correctly installed. | Yes,N/A
button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
button | Verify package using vendor and/or project P&IDs. | Yes,N/A
button | Check that equipment is correctly earthed. | Yes,N/A
button | As-Built drawings completed
textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  | Ohm
signoff | Installed by:
checklist | ITR-E-11 Generator Package (LV)
checkpoint | Generator Package (LV)
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Check terminal boxes and glanding correct. | Yes,N/A
button | Instruments correctly installed. | Yes,N/A
button | Heaters correctly installed. | Yes,N/A
button | Check unit for cleanliness. | Yes,N/A
button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
button | External cabling correctly installed. | Yes,N/A
button | Protection of live parts adequate. | Yes,N/A
button | Main terminal box complete and terminations correct torque. | Yes,N/A
button | Ensure direction of rotation is clearly marked. | Yes,N/A
button | Check gasket and seals are not damaged. | Yes,N/A
button | Unused cable entries are correctly sealed. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | As-builts complete | Yes,N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
textbox | Heater circuit insulation resistance:
signoff | Installed by:
checklist | ITR-E-12 Electrical earthing
Checkpoint | Earthing System
textbox | Electrode Type:
textbox | Electrode Length/Size:
textbox | Location of Electrodes:
textbox | Method of installing electrode:
textbox | Method of attaching to electrode (E.g. Clamp, Cad Weld, Lug/Bolt):
textbox | No. of electrodes:
checkpoint | General
button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
button | Ensure that all metal work is earthed as required. | Yes,N/A
button | Check welding of earth bosses and associated surface finish. | Yes,N/A
button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
button | MEN Link installed: | Yes,N/A
checkpoint | Earthing Conductors
button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
button | Ensure that earth cable identification markings are in place. | Yes,N/A
button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
checkpoint | Test Results
textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
textbox | 3-Wire earth test results (If applicable).
textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
button | As-builts complete | Yes,N/A
signoff | Installed by:
checklist | ITR-E-13 Motors
checkpoint | Motors installation
tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
button | Space heater | Yes,N/A
textbox | Space heater specification (Power (Watts) and Voltage:)
checkpoint - Mandatory photo | Nameplate details correct and in accordance with the data sheet
note | Upload clear photo of nameplate
checkpoint | Checklist items
button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
button | Correct glanding for area classification. | Yes,N/A
button | Holding down bolts fitted correctly. | Yes,N/A
button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
checkpoint | Motor Installation Testing
textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
note | Insulation resistance U, V, W
textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
note | Insulation resistance U, V, W
textbox | Motor continuity between windings
note | Continuity U1-U2, V1-V2, W1-W2.
textbox | Space heater continuity & resistance check
note | Continuity & Insulation resistance results:
textbox | Thermostat or RTD wiring resistance check
note | Resistance:
textbox | Check motor is earthed correctly and record motor earth bond:
checkpoint | Additional checks
tickbox | Winding temperature detector
tickbox | Air temp detectors
tickbox | Bearing temp indicators
tickbox | Vibration Monitors
tickbox | Condensation detector
button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
button | Installation conforms to specification and drawings | Yes,N/A
button | As-Builts complete | Yes,N/A
signoff | Installed by:
checklist | ITR-E-14 Motor Control
checkpoint | General Motor Control
button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
button | Check preservation and transit items are removed | Yes,N/A
button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
button | Check earthing bar and connections are correct and tight | Yes,N/A
button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
button | Check phase identification on power cables is correct and visible | Yes,N/A
button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
button | Check all other nuts and bolts are tight | Yes,N/A
button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
checkpoint | Variable Speed Drives (VSD)
note | Record VSD Details
textbox | Volts (Input) |  |  | V
textbox | Amps (Input) |  |  | A
textbox | Amps (Output) |  |  | A
button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
button | Check control signal cables use twisted pairs | Yes,N/A
button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
button | Check analogue and digital signals are run in separate cables | Yes,N/A
checkpoint | Voltage segregation
button | Distance between input power and motor cable >300mm | Yes,N/A
button | Distance between input power and control signal cable >200mm | Yes,N/A
button | Distance between motor cable and control signal cable >500mm | Yes,N/A
button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
signoff | Installed by:
checklist | ITR-E-15 - UPS Installation
checkpoint -MANDATORY PHOTO | UPS Installation
textbox | Make, Model, Manufacturer, Serial No. (if applicable):
button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Panel IP rating is correct. | Yes,N/A
button | Holding down arrangement and seat alignment correct. | Yes,N/A
button | Panels aligned correctly. | Yes,N/A
button | External bonding correct | Yes,N/A
button | Phase identification correct. | Yes,N/A
button | Instrument, indication lamps & interlocks correct. | Yes,N/A
button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
button | Check Main Isolator and Bypass switch operation | Yes,N/A
button | COM Interface & Mod Link. | Yes,N/A
button | Padlocking facilities correct. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
checkpoint | Test results
textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
signoff | Installed by:
checklist | ITR-E-16 Lightning Protection
checkpoint - Mandatory photo | Lightning Protection Earthing system
button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
button | Check all installed components are firmly secured | Yes,N/A
button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
button | Check earth termination systems are interconnected | Yes,N/A
button | Check isolating and switching devices correctly located | Yes,N/A
button | Check warning signs and diagrams are installed | Yes,N/A
button | Check accessibility for operation and maintenance | Yes,N/A
checkpoint | Test Results
textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  | Ohm
textbox | Earth termination system resistance is correct and record value |  |  | Ohm
textbox | Record the insulation resistance of the electrical installation |  |  | MegaOhm
textbox | Continuity of the main and supplementary equipotential bonding: |  |  | Ohm
signoff | Installed by:
checklist-flat | ITR-E-17 Cable Test Record
checkpoint | Upload completed ITR scans
signoff | Installed by:
checklist-flat | ITR-E-18 Earth Fault Loop Impedance Testing
checkpoint | Upload completed ITR scans
signoff | Installed by:
checklist-flat | ITR-E-19 Test Record for Insulation Resistance
checkpoint | Upload completed ITR scans
signoff | Installed by:
checklist-flat | ITR-E-20 Cadwelds
checkpoint | Mold type, # and cable size identified
dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
dropdown | Select mold # | GTC-312C, XBQ-2C2C, TAC-2C2C, ZC-11159Z, TAC-3D2C, XAC-3D3D, ZC-11160Z, TAC-3D2V, TAC-3D3D
dropdown | Select cable size | 50mm to 16mm Earth Rod, 50mm to 50mm Tee, 50mm to 50mm Cross, 185mm to 185mm Tee, 185mm to 120mm Tee, 185mm to 120mm Cross, 185mm to 185mm Cross, 185mm to 50mm to 50mm Cross, 50mm to 70mm, 50mm to 50mm flex Tee
checkpoint - mandatory photo | Cadweld Visual test
checkpoint - mandatory photo | Cadweld Ductor test
textbox | Result :
note | Pass if <50 micro ohms
checkpoint | Cadweld wrapped in 3M SCOTCH 23 RUBBER or 3M TEMFLEX 1500 GREEN TAPE
checkpoint | GPS coordinates taken
textbox | Coordinates:
signoff | Installed by:
checklist-flat | ITR-E-23A Coaxial Cable
checkpoint | General
button | Cable passes visual inspection | Yes, N/A
button | Verify cable type, size, colour code and tags are as per cable schedule | Yes, N/A
button | Check cable cores correctly identified and labelled. | Yes, N/A
button | Confirm cable routing and segregation is correct. | Yes, N/A
button | Check that cable core polarity is correct | Yes, N/A
button | Glanding / Locknuts correctly installed. | Yes, N/A
textbox | Gland type - from:
textbox | Haz. Area Cert Details.
textbox | Gland type - to:
textbox | Haz. Area Cert Details.
button | All ‘spare’ cores have been made safe and are identified | Yes, N/A
button | Bending radius satisfactory and as per manufacturer's recommendation. | Yes, N/A
checkpoint | Coaxial Cable
button | Check cable terminated with correct crimps. | Yes, N/A
button | Check Continuity | Yes, N/A
button | Check shield/screen correctly made off | Yes, N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
checklist-flat | ITR-E-23B Data Circuit
checkpoint | General
button | Cable passes visual inspection | Yes, N/A
button | Verify cable type, size, colour code and tags are as per cable schedule | Yes, N/A
button | Check cable cores correctly identified and labelled. | Yes, N/A
button | Confirm cable routing and segregation is correct. | Yes, N/A
button | Check that cable core polarity is correct | Yes, N/A
button | Glanding / Locknuts correctly installed. | Yes, N/A
textbox | Gland type - from:
textbox | Haz. Area Cert Details.
textbox | Gland type - to:
textbox | Haz. Area Cert Details.
button | All ‘spare’ cores have been made safe and are identified | Yes, N/A
button | Bending radius satisfactory and as per manufacturer's recommendation. | Yes, N/A
checkpoint | Data Cable
button | Check cable terminated with correct crimps. | Yes, N/A
button | Check Continuity | Yes, N/A
button | Check shield/screen correctly made off | Yes, N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
checklist | ITR-E-25 Cable Lug Installation
checkpoint | Cable lug
button | Appropriate lug for cable size has been used. | Yes,N/A
button | Lug has been correctly seated with no loose copper strands outside of lug. | Yes,N/A
button | Lug has been crimped with 60 tonne crimper. | Yes,N/A
button | Joint sealing paste has been correctly applied to the contact surface of lug | Yes,N/A
checkpoint | Bolts
button | Bolt has been torqued to manufacturers requirements | Yes,N/A
note | If no manufacturer torque spec, use torques below. M8-20NM, M10-40NM, M12-70NM.
textbox | Manufacturers torque requirement (if applicable)
checkpoint | Test Results
textbox | Continuity test results
textbox | Ductor test results if applicable
checkpoint | Test Equipment Used
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat | ITR-E-29 Cat 6 Communication Cable
checkpoint | Common to all circuits
button | Check cable for damage | Yes, N/A
button | Check cable is correctly identified and labelled | Yes, N/A
button | Check glanding/locknuts correctly installed | Yes, N/A
button | Confirm cable routing and segregation is correct | Yes, N/A
button | Confirm to and from destination as per design. | Yes, N/A
checkpoint | Data Circuits
button | Check cable terminated with correct crimps | Yes, N/A
button | Check shield/screen correctly made off | Yes, N/A
button | Check Cat6 end-to-end certification (outlet and cable) | Yes, N/A
checkpoint | Electrical Tests
button | Confirm LAN Link Tester is used to check continuity
textbox | Insert Continuity results: |  | ohm
signoff | Installed by: | Yes, N/A
checklist | ITR-E-30 Earthing Electrodes
textbox | Location of electrodes:
textbox | Electrode length/size:
textbox | Electrode type:
textbox | Method of installing electrode:
textbox | Method of attaching to electrode (E.g. Clamp, cadweld, lug/bolt):
textbox | No. of electrodes:
button | Earth pits correct as per specifications, covers, no damage | Yes,N/A
button | Connections to electrodes are secure | Yes,N/A
button | Structural and equipment earth connections secure | Yes,N/A
button | Earth cable lugs secure, cable passes through concrete in PVC. | Yes,N/A
button | Equipment bonding, connection to main earth bar secure | Yes,N/A
button | Earth electrode identified, MEN linked, installed and labelled | Yes,N/A
checkpoint | Earth Electrode Test and Continuity Tests - Disconnected Electrode
textbox | Electrode 1 |  | Ohm
textbox | Electrode 2 |  | Ohm
textbox | Electrode 3 |  | Ohm
textbox | Electrode 4 |  | Ohm
textbox | Electrode 5 |  | Ohm
textbox | Electrode 6 |  | Ohm
textbox | Electrode 7 |  | Ohm
textbox | Electrode 8 |  | Ohm
checkpoint | Earth Electrode Test and Continuity Tests - Earth Grid Test Results
textbox | HV earth grid |  | Ohm
textbox | LV earth grid |  | Ohm
textbox | Combine HV and LV earth grid |  | Ohm
textbox | Instrument earth |  | Ohm
signoff | Installed by:
checklist | ITR-E-32 Battery
Checkpoint | Batteries
button | Check equipment and nameplate details are correct in accordance with the data sheet and drawings | Yes,N/A
button | Transportation packing and plugs removed | Yes,N/A
button | Battery cells correctly rated and numbered accordingly | Yes,N/A
button | All cells correctly mounted, links tight and shrouds fitted | Yes,N/A
button | Internal cables correctly installed | Yes,N/A
button | Protection of live parts correct and adequate | Yes,N/A
button | Electrolyte level correct in each cell | Yes,N/A
button | Check specific gravity in each battery cell | Yes,N/A
button | Check cleanliness of cells and battery racks | Yes,N/A
button | Verify approved grease applied to battery terminals | Yes,N/A
button | Earthing correct and tight | Yes,N/A
textbox | Verify polarity correct per drawings and record voltage
textbox | Preservation as per supplier instructions
button | Leave equipment with any isolators and/or circuit breakers switched and locked in the off position | Yes,N/A
signoff | Installed by:
checklist | ITR-E-34 Low Voltage Switch Board
Checkpoint | Low Voltage Switch Board
button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | Check holding down/mounting arrangement is correct. | Yes,N/A
button | Check for mechanical damage. | Yes,N/A
button | Confirm that all temporary supports, jumpers and ties have been removed. | Yes,N/A
button | Incoming cables correctly installed, terminated and supported. | Yes,N/A
button | Phase identification correct. | Yes,N/A
button | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Yes,N/A
button | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Yes,N/A
textbox | Bus bar alignment to manufacturer's specification and connecting links tight to specified torque.
button | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Yes,N/A
button | Instruments, indication lamps and interlocks correct. | Yes,N/A
button | Ammeter and current transformer correctly installed. | Yes,N/A
button | Check internals for cleanliness. | Yes,N/A
button | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Yes,N/A
textbox | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms
button | All internal cabling and wiring neat, correct, and undamaged. | Yes,N/A
button | Unused cable entry sealed. | Yes,N/A
button | Heaters correctly installed. | Yes,N/A
button | Confirm that all insulating bushings and barriers are satisfactory. | Yes,N/A
Checkpoint | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages. System KV Test V (dc) Min IR Reading <1.0 500 10 MΩ <2.5 1000 50 MΩ < 4.6 2500 100 MΩ >4.6 5000 250 MΩ
textbox | L1 - Earth |  |  | mega ohms
textbox | L2 - Earth |  |  | mega ohms
textbox | L3 - Earth |  |  | mega ohms
textbox | L1 - L2 |  |  | mega ohms
textbox | L1 - L3 |  |  | mega ohms
textbox | L2 - L3 |  |  | mega ohms
textbox | N - Earth |  |  | mega ohms
signoff | Installed by:
checklist | ITR-E-40 Bus Bar
checkpoint | Bus Bar
button | Check entire Bus Bar and confirm there is no damage | Yes,N/A
note | Please attach photo of Bus Bar
button | Bus Bar alignment is correct | Yes,N/A
button | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. Acceptable Bus Bar Torque Settings: Bolt: M6 M8 M10 M12 M16 Torque: 10Nm 20Nm 30Nm 40Nm 60Nm | Yes,N/A
button | Confirm all transit packing and preservation materials have been removed. | Yes,N/A
button | Confirm Bus Bar clearances conform to manufactures and design requirements. | Yes,N/A
button | Confirm all Bus Bars are secure within the supports. | Yes,N/A
Record the total number of bus bar joints.
textbox | Insert applicable test results
signoff | Installed by:
checklist | ITR-E-45 Local Control Station
checkpoint | Local Control Station
button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Glands correct size and type | Yes,N/A
button | LCS properly supported and accessible | Yes,N/A
button | Spare entries correctly plugged | Yes,N/A
button | Check internal cleanliness | Yes,N/A
button | Check push button/control for mechanical function | Yes,N/A
button | Check connections and terminations tight | Yes,N/A
textbox | Check that LCS is correctly earthed. Test and confirm the earth resistance between LCS and local earth system is less than 1.0
button | Check gasket and seals are installed and not damaged | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | As-Builts complete | Yes,N/A
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
checklist | ITR-E-48 General Lighting
Checkpoint | General Lighting
button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | Operation of emergency lighting fixtures checked | Yes,N/A
button | Mounting arrangement and degree unit is installed is correct | Yes,N/A
button | External cabling is correctly installed and labelled. | Yes,N/A
button | Battery run-down test per manufacturers specification | Yes,N/A
button | Power / load balance on distribution board checked | Yes,N/A
button | Operation of remote lighting control checked | Yes,N/A
button | All spare entries blanked off with correct plugs. | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Conforms to Specifications and Drawings. | Yes,N/A
button | Insulation resistance of final sub-circuits checked | Yes,N/A
button | Operation of photo-electric cell control checked | Yes,N/A
button | Lighting pole is adequately earthed | Yes,N/A
button | Circuit ID fitted to all light switches | Yes,N/A
button | All fittings correctly labelled | Yes,N/A
button | All switching tested and confirmed as correct (two way, intermediate, on/off/auto etc | Yes,N/A
button | As-Built drawings completed | Yes,N/A
checkpoint | Lux Levels
button | Lux levels meet minimum client specifications. (Closed door and measure lux level at darkest point of personnel accessible area) | Yes,N/A
textbox | Lux Results:
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-I-02 Instrument Tubing Installation
checkpoint | Checks Pre-Installation
button | Tubing connection to and from equipment as per drawings. | Yes,N/A
button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
button | Tube fitting size and type confirmed and available | Yes,N/A
section | Checks During and Post-Installation
button | Correct thread compatibility and engagement | Yes,N/A
button | Correct thread tape and sealant used on fittings | Yes,N/A
button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
button | Random check with No-Go gap gauge | Yes,N/A
button | In service leak test performed and passed | Yes,N/A
button | Fitting completion tag completed and applied to each fitting | Yes,N/A
note | Refer to Swagelok book for tube/thread size pressure ratings
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-03 Instrument Pressure/Leak Test
checkpoint | Checklist items
button | Tube identification correct | Yes,N/A
button | Mechanical damage visual check | Yes,N/A
button | Flow direction and instrument orientation correct | Yes,N/A
button | Tubing size and installation correct | Yes,N/A
checkpoint | Testing
note | Verify test pressure and medium is correct per project and manufacture specification prior to test
textbox | Test fluid:
textbox | Test pressure:
textbox | Max design pressure:
dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
textbox | Duration: |  |  | Minutes
button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
button | Check hydraulic lines flushed to project specification. | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-04 Valve & Ancillaries (Pre-Installation)
checkpoint | Equipment
button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
button | Equipment checked for additional items as applicable | Yes,N/A
checkpoint | Valve
textbox | Valve Size:
textbox | Flange type:
button | Material certification correct | Yes,N/A
button | Trim material correct | Yes,N/A
textbox | Rating:
textbox | Service:
button | Body material correct | Yes,N/A
textbox | Leakage class:
checkpoint | Actuator
textbox | Input range: |  |  | kPa
button | Failure action | Yes,N/A
button | Hand wheel operation correct | Yes,N/A
checkpoint | Positioner
textbox | Signal range
textbox | Output range
checkpoint | I/P Converter
textbox | Signal range
textbox | Output range
checkpoint | Filter/Regulator/On-Off Valve
textbox | Range |  |  | kPa
textbox | Pressure setting |  |  | kPa
button | Stroke Time correct | Yes,N/A
textbox | Open |  |  | sec
textbox | Close |  |  | sec
button | Open/Close times conform to commissioning specifications | Yes,N/A
checkpoint | Fail Action
dropdown | Electrical Fail Action | FO, FC, FL
dropdown | Motive Force | FO, FC, FL
checkpoint | Valve Field Calibration and Hysteresis Check
tickbox | Confirm test equipment is within calibration period prior to testing
note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
checkpoint | Proximity Detectors
button | Open switch set, correct mode setting | Yes,N/A
button | Closed switch set, correct mode setting | Yes,N/A
button | Electrical connections and certification correct | Yes,N/A
checkpoint | Solenoid Valve
button | Operation correct | Yes,N/A
button | Electrical connections correct | Yes,N/A
button | Electrical certification correct | Yes,N/A
textbox | Voltage: |  |  | V
button | Pneumatic connections correct | Yes,N/A
textbox | Pneumatic pressure |  |  | kPa
checkpoint | Pilot Valve
button | Pneumatic connections correct | Yes,N/A
button | Operation correct | Yes,N/A
button | Action/Lockup | Yes,N/A
checkpoint | Hydraulic Actuator
textbox | Working pressure
textbox | Manifold pressure
textbox | Fluid type
button | Hydraulic connections correct | Yes,N/A
textbox | Regulator pressure setting
button | Pilot operation correct | Yes,N/A
checkpoint | Accumulator
button | N2 Charge required | Yes,N/A
textbox | N2 Pre-charge pressure
textbox | Pressure switch setting
textbox | Working pressure
textbox | Output range
button | Volume tank & check valve installed correctly | Yes,N/A
checkpoint | Electric Actuator
textbox | Voltage:
button | Electrical certification correct | Yes,N/A
button | Electrical connections correct | Yes,N/A
button | Remote operation correct | Yes,N/A
button | Local hand operation correct | Yes,N/A
button | Torque switches and travel stops set | Yes,N/A
checkpoint | Miscellaneous Equipment
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
textbox | Range:
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-06 Instrument Installation
checkpoint - Mandatory photo | Instrument Installation
button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
button | Vent lines are directed into a safe area. | Yes,N/A
button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
button | Spare entries plugged correctly, using certified plug. | Yes,N/A
button | Instrument earthed in accordance with project specification. | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-07 Instrument Calibration
checkpoint-no-status | Required Data
textbox | Type and Size:
textbox | Make and Model:
textbox | Serial No:
textbox | Instrument Type:
textbox | Instrument designation/equipment no
textbox | Calibration interval
textbox | Calibration method
textbox | Calibrated at
checkpoint | Instrument Power Supply
dropdown | Supply type | VAC, 2 Wire DC, Other, None
textbox | Supply value:
button | Calibration sheet completed and attached below | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-08 Instrument Pre-Commissioning
checkpoint | Checklist items
button | Verify transmitter loop connection - Remove wire on transmitter and confirm at Control System interface | Yes,N/A
button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
checkpoint | Analogue Input:
checkpoint-no-status | Analogue Input:
textbox | Input range & units:
textbox | Indication range & units:
checkpoint-no-status | 0% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 25% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 50% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 75% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 100% Peak
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 75% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 50% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 25% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint-no-status | 0% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | Digital Input/Analogue Alarm Trip Points
checkpoint-no-status | Alarm Lo:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Alarm Lo-Lo:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Alarm Hi:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Alarm Hi-Hi:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint-no-status | Control loop set points correct:
textbox | Set Point 1:
textbox | Set Point 2:
textbox | Set Point 3:
textbox | Set Point 4:
checkpoint | Startup, Shutdown and Override functions
button | Control system graphic display | Yes,N/A
button | Control system point display | Yes,N/A
button | ESD graphic display | Yes,N/A
button | Alarm Recording and Text | Yes,N/A
checkpoint | Additional checks
button | Control system display and alarms are correct as per control functions | Yes,N/A
button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
button | Switch action verified, including power loss | Yes,N/A
button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-09 Commissioning Instruments
checkpoint | Required Data
textbox | Instrument range:
button | Installation complete | Yes,N/A
button | Point-to-point | Yes,N/A
button | Haz. Inspected | Yes,N/A
button | Tag correct | Yes,N/A
button | Hook-up correct | Yes,N/A
checkpoint | Alarms & Set points
checkpoint-no-status | Alarm Lo
textbox | Activated:
checkpoint-no-status | Alarm Lo-Lo
textbox | Activated:
checkpoint-no-status | Alarm Hi
textbox | Activated:
checkpoint-no-status | Alarm Hi-Hi
textbox | Activated:
checkpoint-no-status | Set Point 1
textbox | Activated:
checkpoint-no-status | Set Point 2
textbox | Activated:
checkpoint-no-status | Set Point 3
textbox | Activated:
checkpoint-no-status | Set Point 4
textbox | Activated:
checkpoint | Calibration settings
textbox | Zero
textbox | Range
textbox | Other (Specify)
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-10 Cone and Thread Tubing Installation
checkpoint-no-status | General Data
textbox | Location:
textbox | Duty:
textbox | Reference Drawings/Hook-up drawing:
textbox | Related instrument tag no:
textbox | Tube diameter and wall thickness:
checkpoint | Cone and Thread installation - Stainless fittings
button | Correct thread compatibility and engagement | Yes,N/A
button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
checkpoint-MANDATORY PHOTO | Cone machined face. No defects, lines, bumps etc.
label | Attach photo of cone and thread.
checkpoint-MANDATORY PHOTO | Thread cleanly cut, de-burred and cleaned.
label | Attach photo of collar.
button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
button | Correct Tube nut used for the right sized tube | Yes,N/A
label | Ensure No thread tape or sealant are used on tube nuts | Yes,N/A
button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
button | Ensure Weep hole is unobstructed and clean | Yes,N/A
button | In service leak test performed and passed | Yes,N/A
button | Fitting completion tag completed and applied to each fitting | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-11 Cone and Thread Pressure Testing
checkpoint-no-status | General Data
textbox | Location:
textbox | Duty:
textbox | Reference Drawings:
textbox | Hook-up drawing:
textbox | Related instrument tag no:
textbox | Tube diameter and wall thickness:
checkpoint | Checklist items
button | Tubing orientation as per hook up drawing. | Yes,N/A
button | Checked with a Torque Wrench and marked and tagged | Yes,N/A
button | Ensure Area is barricaded off to restrict unauthorized entry to personnel | Yes,N/A
button | Tube as per specification and hook up drawings. | Yes,N/A
textbox | Max design pressure:
textbox | Test medium used:
textbox | Record Testing pressure:
textbox | Test pressure duration: |  |  | Minutes
textbox | Test leak rate: |  |  | Litres/minute
button | Chart recorder used and attached (where applicable). | Yes,N/A
button | Confirm all Tubing lines have been pigged / cleaned. | Yes,N/A
button | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions. | Yes,N/A
button | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-12 Telecommunications Equipment Panel
checkpoint | Telecommunications Equipment Panel
button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
checklist | ITR-I-13 Temperature Instrument Installation
checkpoint | Temperature Instrument Installation
button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
textbox | Type and Size:
textbox | Make and Model:
textbox | Serial No:
textbox | Instrument designation/equipment no
button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
button | Vent lines are directed into a safe area. | Yes,N/A
button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
button | Spare entries plugged correctly, using certified plug. | Yes,N/A
button | Instrument earthed in accordance with project specification. | Yes,N/A
textbox | Calibration interval
textbox | Calibration method
textbox | Calibrated at
checkpoint | Instrument Power Supply
dropdown | Supply type | VAC, 2 Wire DC, Other, None
textbox | Supply value:
button | Calibration sheet completed and attached below | Yes,N/A
dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
button | Internal depth of thermowell checked and recorded | Yes,N/A
textbox | Depth:
button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
button | Thermowell CE marked | YES,NO
button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-14 Flow Meter Installation
checkpoint | Flow Meter Installation
button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
textbox | Type and Size:
textbox | Make and Model:
textbox | Serial No:
textbox | Instrument designation/equipment no
button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
button | Vent lines are directed into a safe area. | Yes,N/A
button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
button | Spare entries plugged correctly, using certified plug. | Yes,N/A
button | Instrument earthed in accordance with project specification. | Yes,N/A
textbox | Calibration interval
textbox | Calibration method
textbox | Calibrated at
checkpoint | Instrument Power Supply
dropdown | Supply type | VAC, 2 Wire DC, Other, None
textbox | Supply value:
button | Calibration sheet completed and attached below | Yes,N/A
button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-15 Pressure Instrument Installation
checkpoint | Pressure Instrument Installation
button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
textbox | Type and Size:
textbox | Make and Model:
textbox | Serial No:
textbox | Instrument designation/equipment no
button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
button | Vent lines are directed into a safe area. | Yes,N/A
button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
button | Spare entries plugged correctly, using certified plug. | Yes,N/A
button | Instrument earthed in accordance with project specification. | Yes,N/A
textbox | Calibration interval
textbox | Calibration method
textbox | Calibrated at
checkpoint | Instrument Power Supply
dropdown | Supply type | VAC, 2 Wire DC, Other, None
textbox | Supply value:
button | Calibration sheet completed and attached below | Yes,N/A
button | Instrument mounted as per hook-up drawings | Yes,N/A
button | Air line/Impulse line are correct material to site specifications | Yes,N/A
button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
button | Correct bolt size and material/grade used | Yes,N/A
button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
button | Isolation valve installed | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-16 Level Instrument Installation
checkpoint | Level Instrument Installation
button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
textbox | Type and Size:
textbox | Make and Model:
textbox | Serial No:
textbox | Instrument designation/equipment no
button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
button | Vent lines are directed into a safe area. | Yes,N/A
button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
button | Spare entries plugged correctly, using certified plug. | Yes,N/A
button | Instrument earthed in accordance with project specification. | Yes,N/A
textbox | Calibration interval
textbox | Calibration method
textbox | Calibrated at
checkpoint | Instrument Power Supply
dropdown | Supply type | VAC, 2 Wire DC, Other, None
textbox | Supply value:
button | Calibration sheet completed and attached below | Yes,N/A
button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
button | Bolts and studs are to site specification | Yes,N/A
button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
button | Ensure gasket and studs are used as per specifications | Yes,N/A
button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
button | Verify antenna/source are installed correctly | Yes,N/A
button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-I-21 - Instrument Cables
checkpoint | Instrument Cable
button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
button | Check dressing / cleating, cable undamaged | Yes,N/A
button | Cable mechanically protected | Yes,N/A
button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
button | Screen correctly made off | Yes,N/A
button | Glanding / Locknuts correctly installed. | Yes,N/A
textbox | Gland type - from: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Gland type - to: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
signoff | Client Representative:
checklist | Test Equipment Details
checkpoint-no-status | Details
textbox | Make
textbox | Model
textbox | Serial No
textbox | Calibration Expiry Date
checklist | JHA - Job Hazard Analysis
section | Job details
checkpoint-no-status | Job details
date | Date:
textbox | Permit No.
textbox | Job No.
textbox | Site
textbox | Activity Location
textbox | Asset:
textbox | Work Details:
section | Prompts for Hazards - Mark all that apply.
checkpoint-no-status | Prompts for Hazards - Mark all that apply.
tickbox | Sparks/Open flame
tickbox | Disabled safety device(s)
tickbox | Uneven surfaces
tickbox | Fatigue, over-exertion
tickbox | Crane movements
tickbox | Moving/Rotating parts
tickbox | Remote area, working alone
tickbox | Conflicting work/SIMOPS
tickbox | Electrical arc flash
tickbox | Sharp objects/materials
tickbox | Restricted/Difficult Entry/Exit
tickbox | Overhead obstacles
tickbox | Ignition sources (other)
tickbox | Access/Egress
tickbox | Water body
tickbox | Live equipment
tickbox | Slippery surfaces
tickbox | Suspended loads
tickbox | Hazardous substances (chemicals)
tickbox | Use of non-intrinsically safe equipment
tickbox | Weather extremes
tickbox | Moving vehicles
tickbox | Task related noise
tickbox | Engulfment
tickbox | General waste
tickbox | Hazardous waste
tickbox | Hazardous/toxic substance, fumes, gas
tickbox | Flammable materials - Gas, liquids, solids
tickbox | Reduced visibility, lighting
tickbox | Electricity
tickbox | Static electricity
tickbox | Work at height
tickbox | Underground services
tickbox | O2 Deficiency/Excess
tickbox | Temperature extremes
tickbox | Heavy objects
tickbox | Radiation
tickbox | Potential energy - Tension/Compression
tickbox | Flying particles/Dust/Objects
tickbox | Vehicle entry
tickbox | Exposure to process temperatures.
section | Prompts for Initial Consequences - Mark all that apply
checkpoint-no-status | Prompts for Initial Consequences - Mark all that apply
tickbox | Falling/Dropped objects
tickbox | Fall from height
tickbox | Trip/Slip/Fall
tickbox | Gas release
tickbox | Pressure release
tickbox | Struck by object
tickbox | Exceeding tool limits
tickbox | Overloading people
tickbox | Unplanned shutdown
tickbox | Exposure to O2 deficiency/excess
tickbox | Exposure to hazardous substance
tickbox | Entanglement
tickbox | Flying objects
tickbox | Loss of control
tickbox | Loss of containment
tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
tickbox | Loss of structural integrity
tickbox | Equipment failure
tickbox | Uncontrolled ignition source
tickbox | Collision
tickbox | Ignition/Fire
tickbox | Back strain/Injury
tickbox | Burns
tickbox | Heat exhaustion
section | Initial controls - Mark all that apply.
checkpoint-no-status | Initial controls - Mark all that apply.
note | People controls
tickbox | Safety/Fire watch person
tickbox | Barriers/Flagging
tickbox | Warning signs
note | Equipment controls
tickbox | Master tags and locks
tickbox | Scaffolding for access
tickbox | Radio communication
note | Environmental controls
tickbox | Ventilation
tickbox | Lighting
tickbox | Gas Testing
note | High risk controls
tickbox | WSCS Work permit
tickbox | WSCS Certificates
tickbox | Critical lift/Fall protection plan
tickbox | Specialised PPE
tickbox | Spill kit
tickbox | Fire extinguisher
section | Signatures
checkpoint-no-status | Signatures
signoff | Applicant signature
checklist | JHA - Job Step
section | Task Step - add task step for each individual task
checkpoint-no-status | Task Step - add task step for each individual task
date | Date:
textbox | Task step number (eg. Step 1, Step 2 etc):
textbox | Task details:
textbox | Hazards:
dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
textbox | Potential consequence:
textbox | Controls:
textbox | Recovery steps:
dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist | Toolbox Meeting
section | Toolbox meeting
checkpoint-no-status | Toolbox meeting
date | Date:
textbox | Meeting location:
textbox | Meeting conducted by:
textbox | Meeting attendees:
textbox | Today's work scope/Hazards
textbox | Hazard controls:
signoff | PICWS Signoff
checklist | As-Built Drawings
checkpoint-no-status | As-Built Drawings - attach scanned documents
checklist-flat | Certificate of compliance (COC)
checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-flat | Record of Inspection (ROI)
checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist | MSDS
checkpoint | Please Upload MSDS Sheets
checklist | Entec Daily Report
checkpoint | Daily Report
date | Date:
textbox | Site:
textbox | Work completed:
textbox | Issues:
textbox | Weather:
textbox | Labour:
textbox | Plant & Equipment used:
signoff | Signed/Approved:
checklist | ITR-E-19 HV Cable Install
checkpoint | HV Cable Install
button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
button | Check dressing / cleating, cable undamaged | Yes,N/A
button | Check cable cores correctly identified and labelled. | Yes,N/A
button | Check cable is terminated correctly | Yes,N/A
button | Cable has been installed as per client specification | Yes,N/A
button | No visible damage to sheath | PASS,FAIL
dropdown | Cable Voltage | 11kV,33kV
textbox | Temperature:
textbox | Cable Point to Point:
checkpoint - mandatory photo | Electrical Tests
note | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ. Please insert photo of test results.
textbox | R-WBE |  |  | GΩ
textbox | W-RBE |  |  | GΩ
textbox | B-RWE |  |  | GΩ
textbox | One Core |  |  | GΩ
checkpoint-no-value | Sheath Integrity Test
textbox | Test Duration:
textbox | Test Voltage: |  |  | GΩ
textbox | Result (GΩ):
checkpoint-no-value | Test Equipment Details
dropdown | Make | PHENIX
dropdown | Model | PM10A
dropdown | Serial No | 20-4331
textbox | Calibration Expiry Date
checkpoint-no-value | Installer Sign-off
signoff | Installed by:
checklist | ITR-E-56 Fire Detection System
checkpoint | Fire Detection System
button | Fire Panel ITR has been completed | Yes,N/A
textbox | Tag Numbers:
button | Smoke alarms have been installed as per specification | Yes,N/A
button | Smoke alarms are ALL operational | Yes,N/A
button | Alarm speaker has been installed per specifications | Yes,N/A
button | Alarm speaker is operational | Yes,N/A
button | Fire alarm beacon has been installed per specification | Yes,N/A
button | Fire alarm beacon is operational | Yes,N/A
button | Manual call point has been installed per specification | Yes,N/A
button | Manual call point is operational | Yes,N/A
button | Installations are all unobstructed | Yes,N/A
button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | All installations have identification tags | Yes,N/A
button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
button | E.O.L has been installed as is operational | Yes,N/A
textbox | Other fire system installations have been installed correctly:
button | As-builts complete. | Yes,N/A
checkpoint | Functional Check
textbox | Selt test:
textbox | Alarm Operation:
textbox | Fault relay operation:
textbox | Measured output (clear path):
textbox | Measured output (blocked path):
textbox | Measured output (filter in place):
textbox | Confirm ENTEC witness of installers testing
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist | ITR-E-55 HVAC System
checkpoint | HVAC System
textbox | Model:
textbox | Manufacturer:
textbox | Serial and Tag Numbers:
button | No mechanical damage and paintwork is in good condition | Yes,N/A
button | Operation of units verified | Yes,N/A
button | Mounting arrangement is correct | Yes,N/A
button | External cabling is correctly installed and labelled | Yes,N/A
button | HVAC unit isolator is installed and operational | Yes,N/A
button | Remote holders are installed with remotes inside them | Yes,N/A
button | Units are labelled with appropriate ID’s | Yes,N/A
button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | Conforms to Specifications and Drawings | Yes,N/A
button | Any applicable control system configuration has been checked and is functional as per design | Yes,N/A
textbox | Confirm ENTEC witness of installers testing
signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)

## Examples
Command | Description
checklist | complex checklist with progress bar
checklist-flat | simple checklist
section | breaks checklist into sections
checkpoint | Pass/Fail/NA checkpoint
checkpoint-no-status
textbox | Textbox for inputting data for above checkpoint/section
dropdown | Select from a dropdown range of options. Enter options in "Values" tab separated by commas eg. Item 1, Item 2, Item 3
date | users can select date from a calendar
label | Creates a label for relevant checkpoint/section, good for additional notes or instruction e.g "Test 230v circuits at 500VDC for IR test"
button | Buttons with defined labels, enter options in "Values" tab separated by commas eg. Yes, No or option A, option B, option C, etc
signoff | creates touchscreen signature input section, for signing off documents
tickbox | simple tickbox, in final export it appears as "Yes" when ticked and "No" when unticked.